## Slide 1: EE 303 Energy Systems and Power Electronics Magnetics, Transformer and Harmonics
GRA: Prashant Tiwari
Advisor: Dr. Zhaoyu Wang
1113 Coover Hall, Ames, IA
wzy@iastate.edu
ECpE Department

## Slide 2: Ampere’s Law
Ampere's circuital law, discovered by Andre-Marie Ampere in 1826, relates the integrated magnetic field around a closed loop to the electric current passing through the loop:
In which,
Line integral along a closed path ( is tangent to the path) Algebraic sum of current linked by the path Magnetic Field Intensity (amp-turns/meter) Vector differential path length (meters) magnetomotive force (amp-turns)
ECpE Department

## Slide 3: What is Line Integral?
ECpE Department
Line integrals are a generalization of traditional integration.
Integration along the -axis
Integration along a general path which could be closed
Ampere's law is most useful in cases of symmetry, such as with an infinitely long line.

## Slide 4: Magnetic Flux Density
ECpE Department
Magnetic fields are usually measured in terms of flux density, , whose unit is Tesla or Gauss , and .
For a linear magnetic material:
where is the called the permeability.
permeability of free space
relative permeability for air

## Slide 5: Contd…
ECpE Department
Total flux passing through a surface is:
Where, is a vector with direction normal to the surface.
If flux density is uniform and perpendicular to an area , then:

## Slide 6: Magnetic Fields from Single Wire
ECpE Department
Q. Assume we have an infinitely long wire with current of . How much magnetic flux passes through a 1-meter square, located between 4 and 5 meters from the wire?

## Slide 7: Magnetic Fields from Single Wire
ECpE Department
Q. Assume we have an infinitely long wire with current of . How much magnetic flux passes through a 1 meter square, located between 4 and 5 meters from the wire?
Solution:
The easiest way to solve the problem is to take advantage of symmetry. For an integration path we will choose a circle with a radius of .

## Slide 8: Contd…
ECpE Department
For reference, the earth's magnetic field is about Gauss (Central US).

## Slide 9: Flux Linkages and Faraday’s Law
ECpE Department
Flux linkage, , is defined from Faraday's law:
where voltage and flux linkage.
The flux linkage is the sum of the flux cut (linked) by each turn of wire. If each turn cuts (or links) flux , the total flux linkage for turns must be .

## Slide 10: Inductance
ECpE Department
For a linear magnetic system in which
we can define the inductance, L, to be the constant relating the current and the flux linkage
where, the unit of L is Henry (H).

## Slide 11: Inductance Example
ECpE Department
Calculate the inductance of an turn coil wound tightly on a toroidal iron core that has a radius of and a cross-sectional area of A. Assume:
all flux is within the coil.
all flux links each turn.

## Slide 12: Inductance Example: Solution
ECpE Department
path length is

## Slide 13: Transformers
ECpE Department
Power systems are characterized by many different voltage levels, ranging from down to volts.
Transformers are used to transfer power between different voltage levels.
The ability to inexpensively change voltage levels is a key advantage of ac systems over dc systems.

## Slide 14: How do they look like?
ECpE Department

## Slide 15: Transmission Transformers
ECpE Department

## Slide 16: Distribution Transformers
ECpE Department

## Slide 17: Ideal Transformers
First, we review the voltage/current relationships for an ideal transformer assuming
no real power losses,
magnetic core has infinite permeability,
no leakage flux.
We define the "primary" side of the transformer as the side that 17 usually takes power, and the secondary as the side that usually delivers power.
Primary is usually the side with the higher voltage, but may be the low voltage side on a generator step-up transformer.
ECpE Department

## Slide 18: Ideal Transformer Relationships
ECpE Department
Assume we have flux in magnetic material. Then:
Note:

## Slide 19: Current/Voltage Relationships
ECpE Department
To get the current relationships, use ampere’s law:
where,
So, the equation can also be written as,
or,
or,

## Slide 20: Contd…
ECpE Department
or,
Assuming uniform flux density in the core,
If is infinite, then
Hence,

## Slide 21: Contd…
ECpE Department
Note:
Polarity:
Current owing into a dot on the primary winding will induce a current owing out of the dot on the corresponding secondary winding.
Depending on how the windings are connected to the bushings, the polarities can be additive or subtractive.

## Slide 22: Contd…
ECpE Department
As we have derived the expression,
We can write in the matrix form as,

## Slide 23: Impedance Transformation Example
ECpE Department
Calculate the primary voltage and current for an impedance load on the secondary.
Solution:
Then,
Thus,
This is the equivalent impedance in primary side.

## Slide 24: Real Transformers
ECpE Department
Real Transformers:
have losses,
have leakage flux,
have finite permeability of magnetic core.

## Slide 25: Transformer Losses
ECpE Department
Real power losses are due to resistance in windings and core losses due to eddy currents and hysteresis.
Eddy currents arise because of changing flux in core. Eddy currents are reduced by laminating the core.
Hysteresis losses are proportional to area of curve and the frequency. These losses are reduced by using material with a thin curve.

## Slide 26: Effect of Leakage Flux
ECpE Department
Not all flux is within the transformer core.
Assuming a linear magnetic medium, we get:
and
Thus,
Resistance of the wire
Voltage induced by
Voltage induced by flux leakage

## Slide 27: Effect of Finite Core Permeability
ECpE Department
Finite core permeability means a non-zero is required to maintain in the core:
This value is usually modelled as magnetizing current.
;
where is the magnetizing current.

## Slide 28: Transformer Equivalent Circuit
ECpE Department
Using the previous relationships, we can derive an equivalent circuit model for the real transformer.

## Slide 29: Contd…
ECpE Department

## Slide 30: Contd…
ECpE Department

## Slide 31: Contd…
ECpE Department
This model is further simplified by referring all impedances to the primary side:

## Slide 32: Contd…
ECpE Department
Moreover, since the impedance of the parallel branch is so high, we can approximate the equivalent circuit:

## Slide 33: Calculation of Model Parameters
ECpE Department
The parameters of the model are determined based upon:
Nameplate data: Gives the rated voltages and power.
Open circuit test: Rated voltage is applied to primary with secondary open; measure the primary current and losses (the test may also be done applying the voltage to the secondary, calculating the values, then referring the values back to the primary side).
Short circuit test: With secondary shorted, apply voltage to primary to get rated current to flow; measure voltage and losses.

## Slide 34: Open Circuit Test
ECpE Department
The open circuit test is conducted to determine the parameters of the magnetizing branch: and . In this test, usually the high-voltage side is open-circuited, and the rated voltage is applied to the low-voltage side. Then, the current, voltage, and power at the low-voltage side are measured by using a voltmeter, an ammeter, and a watt-meter. In such a case, the voltage drop in the leakage inductance and winding resistance is negligible due to very low primary current. Therefore, the transformer equivalent circuit is as shown below.

## Slide 35: Simplified Equivalent Circuit
ECpE Department

## Slide 36: Calculation of Model Parameters
ECpE Department
The parameters of the model are determined based on:
Nameplate data: Gives the rated voltages and power
Open Circuit Test:
Rated voltage is applied to primary with secondary open;
Measure the primary current and losses (the test may also be done applying the rated voltage to the secondary, calculating the values, then referring the values back to the primary side).
Short Circuit Test:
With secondary shorted, apply voltage to primary to get rated current to flow; Measure voltage and losses.

## Slide 37: Open Circuit Test
ECpE Department
The watt-meter shows the core loss. Therefore,
Moreover, the magnitude of the admittance of the branch is:

## Slide 38: Short Circuit Test
ECpE Department
The short circuit test is conducted to determine the parameters of the windings: and . In this test, usually the low-voltage side is short-circuited, and a reduced voltage is applied to the high-voltage side such that the rated current flows. Then, the current, voltage, and power at the high-voltage side are measured by using a voltmeter, an ammeter, and a watt-meter. In such a case, the magnetizing branch can be neglected since the magnetizing current is negligible compared to the rated current. Therefore, the transformer equivalent circuit is as shown below.

## Slide 39: Contd…
ECpE Department
The watt-meter shows the winding loss. Thus,
The magnitude of the winding impedance is:
Therefore,

## Slide 40: Contd…
ECpE Department
It must be noted that the values obtained in the short circuit test are at the high-voltage side, while the parameters obtained in the open circuit test are at the low-voltage side. Therefore, to obtain the final equivalent model, all parameters must be transformed to either the low-voltage or the high-voltage side.

## Slide 41: Transformer Parameters Calculation Example
ECpE Department
These data were obtained when open-circuit and short circuit tests were conducted on a single-phase transformer with the power rating of with the rated frequency of . The rated voltages of the high-voltage and low-voltage sides are and , respectively.
 | Voltage (V) | Current (A) | Power (W)
HV Winding Open Circuit | 240 |  | 180
LV Winding Short Circuit | 50 |  | 600
 | Voltage (V) | Current (A) | Power (W)
HV Winding Open Circuit | 240 |  | 180
LV Winding Short Circuit | 50 |  | 600
Calculate the equivalent circuit of the transformer referred to the low voltage side.

## Slide 42: Solution:
ECpE Department
 | Voltage (V) | Current (A) | Power (W)
HV Winding Open Circuit | 240 |  | 180
LV Winding Short Circuit | 50 |  | 600
 | Voltage (V) | Current (A) | Power (W)
HV Winding Open Circuit | 240 |  | 180
LV Winding Short Circuit | 50 |  | 600
Using the open-circuit test data, and can be calculated:
.
Then, .

## Slide 43: Contd…
ECpE Department
 | Voltage (V) | Current (A) | Power (W)
HV Winding Open Circuit | 240 |  | 180
LV Winding Short Circuit | 50 |  | 600
 | Voltage (V) | Current (A) | Power (W)
HV Winding Open Circuit | 240 |  | 180
LV Winding Short Circuit | 50 |  | 600
Using the short-circuit test data, and can be calculated:
.
Then, .

## Slide 44: Contd…
ECpE Department
It must be noted that and are at the high-voltage side. Since the equivalent model at the low-voltage side is asked, and must be referred to the low voltage side.
Then,

## Slide 45: Single Phase Transformer Applications
ECpE Department
Single phase transformers are commonly used in residential distribution systems. Most distribution systems are 4 wire, with a grounded, common neutral.

## Slide 46: Transformer Test Example
ECpE Department
Determine the model parameters for a single phase, transformer with the following test data:
    Short circuit: 30 kV, with 500 kW losses
    Open circuit: 20 amps, with 10 kW losses
Determine the model parameters.

## Slide 47: Contd…
ECpE Department
From the short circuit test
,
Hence

## Slide 48: Contd…
ECpE Department
From the open circuit test

## Slide 49: Phase Transformers Interconnections
ECpE Department
There are 4 different ways to connect transformers.

## Slide 50: Contd…
ECpE Department

## Slide 51: Y-Y Connection
ECpE Department
The top figure shows the wiring of the transformer where terminals a′, b′, and c′ of the primary windings are connected to a common point called neutral n.
The secondary windings are similarly connected.
A more convenient schematic is the one at the bottom of the figure.

## Slide 52: Y-Y Connection
ECpE Department
The turns ratio of the transformer is , while the line-to-line voltage ratio of the transformer is .
The current ratio is the inverse of the turns ratio.
Y-Y connections are common in transmission systems.
Key advantages are the ability to ground each side and there is no phase shift introduced.

## Slide 53: 𝚫 - 𝚫 Connection
ECpE Department
NOTE that the currents in the transformer windings are phase currents, and the currents in the circuit feeding the transformers are the line currents.

## Slide 54: 𝚫 - 𝚫 Connection
ECpE Department
The turns ratio of the transformer is . The voltage ratio of the transformer is the ratio of the voltages , which are the same as the ratio of the line-to-line voltages in the delta configuration.
Keep in mind that the voltage per turn is constant in any winding. Hence,
Using the magnetomotive force equation, we can compute the current ratio
Key disadvantage is D-D connections can not be grounded; not commonly used.

## Slide 55: 𝚫 - Y Connection
ECpE Department
The analysis of the wye–delta transformer requires some attention when computing the various ratios.
The voltage across is the phase voltage of the primary circuit and the voltage across is the line-to-line voltage of the secondary circuit . Since the voltage turns ratio as

## Slide 56: 𝚫 - Y Connection
ECpE Department
Similarly, the current through is the line current of the primary circuit and the current through is the phase current of the secondary winding .
Hence, we can compute the current ratio using the ampere-turn equation.

## Slide 57: 𝚫 - Y Connection: V/I Relationships
ECpE Department
For Voltage, we get,
For Current, we get,

## Slide 58: Example 1:
ECpE Department
A transformer has a voltage ratio of . Compute the following:
Winding voltages
Turns ratio
Line currents in the primary and secondary circuits
Phase currents of the transformer

## Slide 59: Example 1: Solution
ECpE Department
1.
  The primary windings of the transformer are connected in wye. Hence, the voltage across the winding is
  The secondary windings are connected in delta. Hence, the winding voltage is equal to the line-to-line voltage
The turns ratio is the ratio of the voltages of the windings

## Slide 60: Example 1: Solution
ECpE Department
3.
  The line current in the primary circuit is
  The line current in the secondary circuit is
.
  Since the primary windings are connected in wye, the phase current of the primary winding is the same as the line current of the primary circuit.
  The secondary windings are connected in delta, hence the phase current of the secondary winding is

## Slide 61: Example 2
ECpE Department
Generator with -Y step up transformer. Transformer is made of identical transformers with . Each generator phase is modeled as a Thevenin equivalent circuit. The transformer delivers at lagging power factor at to the bus.
Find the primary current, primary voltage , and complex power supplied by the generator.

## Slide 62: Example 2: Solution
ECpE Department
Find the primary current, primary voltage , and complex power supplied by the generator.
Solution,

## Slide 63: Contd…
ECpE Department

## Slide 64: Transformer Efficiency
ECpE Department
The efficiency of a transformer is given by,
The losses of the transformer are due to R1, R2, and Ro. The losses in R1 and R2 are the winding losses, and are named copper losses Pcu (the windings are made of copper material). The loss in Ro is known as iron loss Piron (the core is made of iron).

## Slide 65: Voltage Regulation
ECpE Department
Mathematically,
The voltage regulation of a transformer indicates the voltage reduction due to various parameters of the transformer.
is the magnitude of the open circuit voltage measured at the load terminals
is the magnitude of the voltage at the load terminals when the rated current is delivered to the load
At no load, (open circuit)

## Slide 66: Per Unit Change of Base Power
ECpE Department
The base power is usually called "system base“.
Parameters for equipment are often given using power rating of equipment as the base power.
Also called "transformer base", "generator base", etc.

## Slide 67: Thank You!
ECpE Department