## Slide 1: EE455 Introduction to Energy Distribution Systems
Dr. Zhaoyu Wang
1113 Coover Hall, Ames, IA
wzy@iastate.edu
ECpE Department

## Slide 2
Modeling Three-Phase Transformers
Acknowledgement: The slides are developed based in part on Distribution System Modeling and Analysis, 4th edition, William H. Kersting, CRC Press, 2017

## Slide 3
Three-Phase Transformer Models
Three-phase transformer banks are found in the distribution substation where the voltage is transformed from the transmission or subtransmission level to the distribution feeder level.
In most cases, the substation transformer will be a three-phase unit perhaps with high-voltage no-load taps and, perhaps, low-voltage load tap changing (LTC).
For a four-wire wye feeder, the most common substation transformer connection is the delta–grounded wye. A three-wire delta feeder will typically have a delta–delta transformer connection in the substation.
Three-phase transformer banks out on the feeder will provide the final voltage transformation to the customer's load. A variety of transformer connections can be applied. The load can be pure three-phase or a combination of single-phase lighting load and a three-phase load such as an induction motor.
In the analysis of a distribution feeder, it is important that the various three-phase transformer connections be modeled correctly.

## Slide 4
Three-Phase Transformer Models
Unique models of three-phase transformer banks applicable to radial distribution feeders will be developed. Models for the following three-phase connections are included:
•Delta–grounded wye
•Ungrounded wye–delta
•Grounded wye–delta
•Open wye–open delta
•Grounded wye–grounded wye
•Delta–delta
•Open delta–open delta

## Slide 5
Introduction
Fig.1 defines the various voltages and currents for all three-phase transformer banks connected between the source-side node n and the load-side node m.
Fig.1 General three-phase transformer bank

## Slide 6
Introduction
In Fig.1, the models can represent a step-down (source side to load side) or a step-up (source side to load side) transformer bank. The notation is such that the capital letters A, B, C, and N will always refer to the source side (node n) of the bank and the lower case letters a, b, c, and n will always refer to the load side (node m) of the bank. It is assumed that all variations of the wye–delta connections are connected in the “American Standard Thirty Degree” connection. The described phase notation and the standard phase shifts for positive sequence voltages and currents are
Fig.1 General three-phase transformer bank
Step-down connection
by
(1)
by
(2)
Step-up connection
by
(3)
by
(4)

## Slide 7
Generalized Matrices
The models to be used in power-flow and short-circuit studies are generalized for the connections in the same form as have been developed for line segments and voltage regulators. In the “forward sweep” of the “ladder” iterative technique, the voltages at node m are defined as a function of the voltages at node n and the currents at node m. The required equation is
(5)
In the “backward sweep” of the ladder technique, the matrix equations for computing the voltages and currents at node n as a function of the voltages and currents at node m are given by
(6)
(7)

## Slide 8
Generalized Matrices
(5)
(7)
In Equations (5) through (7), the matrices [VLNABC] and [VLNabc] represent the line-to-neutral voltages for an ungrounded wye connection or the line-to-ground voltages for a grounded wye connection.
For a delta connection, the voltage matrices represent “equivalent” line-to-neutral voltages. The current matrices represent the line currents regardless of the transformer winding connection.
In the modified ladder technique, Equation (5) is used to compute new node voltages downstream from the source using the most recent line currents. In the backward sweep, only Equation (7) is used to compute the source-side line currents using the newly computed load-side line currents.
(6)

## Slide 9: Transformer model
(8.5)
(8.7)

## Slide 10: Transformer model
 | Step-down | Step-up | Step-down | 
 |  | [] |  | []

## Slide 11
Delta-Grounded Wye Step-Down Connection
The delta–grounded wye step-down connection is a popular connection that is typically used in a distribution substation serving a four-wire wye feeder system. Another application of the connection is to provide service to a load that is primary single phase. Because of the wye connection, three single-phase circuits are available thereby making it possible to balance the single-phase loading on the transformer bank.
Three single-phase transformers can be connected delta–grounded wye in a “standard thirty degree step-down connection” as shown in Fig.2.
Fig.2 Standard delta-grounded wye connection with voltage

## Slide 12
Voltages
The positive sequence phasor diagrams of the voltages in Fig.2 show the relationships between the various positive sequence voltages. Care must be taken to observe the polarity marks on the individual transformer windings. In order to simplify the notation, it is necessary to label the “ideal” voltages with voltage polarity markings as shown in Fig.2. Observing the polarity markings of the transformer windings, the voltage Vta will be 180° out of phase with the voltage VCA and the voltage Vtb will be 180° out of phase with the voltage VAB. Kirchhoff's voltage law (KVL) gives the line-to-line voltage between phases a and b as
Fig.2 Standard delta-grounded wye connection with voltage
(8)
The phasors of the positive sequence voltages of Equation (8) are shown in Fig.2.

## Slide 13
Voltages
The magnitude changes between the voltages can be defined in terms of the actual winding turns ratio (nt). With reference to Fig.2, these ratios are defined as follows:
(9)
With reference to Fig.2, the line-to-line voltages on the primary side of the transformer connection as a function of the ideal secondary side voltages are given by
;
(10)
where
Fig.2 Standard delta-grounded wye connection with voltage

## Slide 14
Voltages
;
(10)
Equation (10) gives the primary line-to-line voltages at node n as a function of the ideal secondary voltages. However, what is needed is a relationship between “equivalent” line-to-neutral voltages at node n and the ideal secondary voltages. The question is how is the equivalent line-to-neutral voltages determined knowing the line-to-line voltages? One approach is to apply the theory of symmetrical components.
The known line-to-line voltages are transformed to their sequence voltages by
(11)
where

## Slide 15
Voltages
;
(13)
By definition, the zero sequence line-to-line voltage is always zero. The relationship between the positive and negative sequence line-to-neutral and line-to-line voltages is known. These relationships in matrix form are given by
where
t
Since the zero sequence line-to-line voltage is zero, the (1,1) term of the matrix [T] can be any value. For the purposes here, the (1,1) term is chosen to have a value of 1.0. Knowing the sequence line-to-neutral voltages, the equivalent line-to-neutral voltages can be determined.

## Slide 16
Voltages
;
(13)
The equivalent line-to-neutral voltages as a function of the sequence line-to-neutral voltages are
(14)
Substitute Equation (13) into Equation (14):
(15)
(11)
Substitute Equation (11) into Equation (15):
(16)
where
(17)

## Slide 17
Voltages
(16)
(17)
Equation (17) provides a method of computing equivalent line-to-neutral voltages from a knowledge of the line-to-line voltages. This is an important relationship that will be used in a variety of ways as other three-phase transformer connections are studied.
To continue on, Equation (16) can be substituted into Equation (10):
(10)
(18)
where
(19)

## Slide 18
Voltages
(19)
Equation (19) defines the generalized [at] matrix for the delta–grounded wye step-down connection.
The ideal secondary voltages as a function of the secondary line-to-ground voltages and the secondary line currents are
(20)
where
(21)
Note in Equation (21) there is no restriction that the impedances of the three transformers be equal.

## Slide 19
Voltages
(20)
(18)
Substitute Equation (20) into Equation (18):
(22)
where
(23)

## Slide 20
Voltages
The generalized matrices [at] and [bt] have now been defined. The derivation of the generalized matrices [At] and [Bt] begins with solving Equation (10) for the ideal secondary voltages:
;
(10)
(24)
The line-to-line voltages as a function of the equivalent line-to-neutral voltages are
(25)
where
(26)

## Slide 21
Voltages
(24)
(25)
Substitute Equation (25) into Equation (24):
(27)
where
(28)
Substitute Equation (20) into Equation (27):
(20)
(29)

## Slide 22
Voltages
(29)
Rearrange Equation (29)
(30)
where
(31)
Equation (22) is referred to as the “backward sweep voltage equation” and Equations (30) is referred to as the “forward sweep voltage equation.” Equations (22) and (30) apply only for the step-down delta–grounded wye transformer. Note that these equations are in exactly the same form as those derived in earlier chapters for line segments and step-voltage regulators.
(22)

## Slide 23
Current
The thirty degree connection specifies that the positive sequence current entering the H1 terminal will lead the positive sequence current leaving the X1 terminal by 30°. Fig.3 shows the same connection as Fig.2 but with the currents instead of the voltages displayed.
Fig.3 Delta-grounded wye connection with current

## Slide 24
Current
As with the voltages, the polarity marks on the transformer windings must be observed for the currents. For example, in Fig.3, the current Ia is entering the polarity mark on the low-voltage winding so the current IAC flowing out of the polarity mark on the high-voltage winding will be in phase with Ia. This relationship is shown in the phasor diagrams for positive sequence currents in Fig.3.
Fig.3 Delta-grounded wye connection with current

## Slide 25
Current
The line currents can be determined as a function of the delta currents by applying Kirchhoff's current law (KCL):
(32)
In condensed form, Equation (32) is
(33)
where
The matrix equation relating the delta primary currents to the secondary line currents is given by
(34)
(35)

## Slide 26
Current
(33)
(35)
Substitute Equation (35) into Equation (33):
(36)
(37)
where
(38)

## Slide 27
Current
(36)
Equation (36) (referred to as the “backward sweep current equations”) provides a direct method of computing the phase line currents at node n knowing the phase line currents at node m. Again, this equation is in the same form as that previously derived for three-phase line segments and three-phase step-voltage regulators.
The equations derived in this section are for the step-down connection. Section 8.4 summarizes the matrices for the delta–grounded wye step-up connection.

## Slide 28
Example 1
In the example system of Figure 4, an unbalanced constant impedance load is being served at the end of a 1 mile section of a three-phase line. The 1 mile long line is being fed from a substation transformer rated 5000 kVA, 115 kV delta–12.47 kV grounded wye with a per-unit impedance of 0.085 85.
The phase conductors of the line are 336,400 26/7 ACSR with a neutral conductor 4/0 ACSR. The configuration and computation of the phase impedance matrix are given in Example 4.1. From that example, the phase impedance matrix was computed to be
Fig.4 Example system

## Slide 29
Example 1
The general matrices for the line are
The transformer impedance needs to be converted to per unit referenced to the low-voltage side of the transformer. The base impedance is
The transformer impedance referenced to the low-voltage side is
31.1 0.2304+j2.6335
The transformer phase impedance matrix is

## Slide 30
Example 1
The unbalanced constant impedance load is connected in grounded wye. The load impedance matrix is specified to be
The unbalanced line-to-line voltages at node 1 serving the substation transformer are given as
A. Determine the generalized matrices for the transformer. The “transformer turn's” ratio is

## Slide 31
Example 1
From Equation (19)
(19)
From Equation (23)
(23)

## Slide 32
Example 1
From Equation (37)
From Equation (28)
(37)
(28)

## Slide 33
Example 1
From Equation (31)
(31)

## Slide 34
Example 1
B. Given the line-to-line voltages at node 1, determine the “ideal” transformer voltages. From Equation (27),

## Slide 35
Example 1
C. Determine the load currents.
Since the load is modeled as constant impedances, the system is linear and the analysis can combine all of the impedances (transformer, line, and load) to an equivalent impedance matrix. KVL gives
The line current can now be computed:

## Slide 36
Example 1
D. Determine the line-to-ground voltages at the load in volts and on a 120 V base:
The load voltages on a 120 V base are
The line-to-ground voltage at node 2 are

## Slide 37
Example 1
E. Using the backward sweep voltage equation, determine the equivalent line-to-neutral voltages and the line-to-line voltages at node 1:
It is always comforting to be able to work back and compute what was initially given. In this case, the line-to-line voltages at node 1 have been computed and the same values result that were given at the start of the problem.

## Slide 38
Example 1
F. Use the forward sweep voltage equation to verify that the line-to-ground voltages at node 2 can be computed knowing the equivalent line-to-neutral voltages at node 1 and the currents leaving node 2:
These are the same values of the line-to-ground voltages at node 2 that were determined working from the load toward the source.
Example 8.1 has demonstrated the application of the forward and backward sweep equations. The example also provides verification that the same voltages and currents result working from the load toward the source or from the source toward the load.
In Example 8.2, the system of Example 8.1 is used only this time the source voltages at node 1 are specified and the three-phase load is specified as constant PQ. Because this makes the system nonlinear, the ladder iterative technique must be used to solve for the system voltages and currents.

## Slide 39
Example 2
Use the system of Example 8.1. The source voltages at node 1 are
The wye-connected loads are
The complex powers of the loads are computed to be

## Slide 40
Example 2
The ladder iterative technique must be used to analyze the system. A simple Mathcad® program is shown in Fig.5.
Fig.5 Mathcad® program

## Slide 41
Example 2
Note in this program that in the forward sweep the secondary transformer voltages are first computed and then those are used to compute the voltages at the loads. At the end of the routine, the newly calculated line currents are taken back to the top of the routine and used to compute the new voltages. This continues until the error in the difference between the two most recently calculated load voltages are less than the tolerance. As a last step, after conversion, the primary currents of the transformer are computed.
After nine iterations, the load voltages and currents are
The primary currents are

## Slide 42
Example 2
The magnitude of the load voltages on a 120 V base are
Needless to say, these voltages are not acceptable. In order to correct this problem, three step-voltage regulators can be installed at the secondary terminals of the substation transformer as shown in Fig.6.
Fig.6 Voltage regulators installed
Using the method as outlined in Chapter 7, the final steps for the three regulators are

## Slide 43
Example 2
The regulator turns ratios are
The regulator matrices are

## Slide 44
Example 2
At the start of the Mathcad routine, the following equation is added:
In the Mathcad routine, the first three equations inside the n loop are
At the end of the loop, the following equations are added:
With the three regulators installed, the load voltages on a 120 V base are
As can been seen from this example, as more elements of a system are added, there will be one equation for each of the system elements for the forward sweep and backward sweeps. This concept will be further developed in later chapters.

## Slide 45
Delta-Grounded Wye Step-Up Connection
Fig.7 shows the connection diagram for the delta–grounded wye step-up connection.
Phasor diagrams for the voltages and currents are also shown in Fig.6. Note that the high-side line-to-line voltage leads the low-side line-to-line voltage and the same can be said for the high- and low-side line currents.
The development of the generalized matrices follows the same procedure as was used for the step-down connection. Only two matrices differ between the two connections.
Fig.7 Delta-grounded wye step-up connection

## Slide 46
Delta-Grounded Wye Step-Up VS Step-Down Connections
Delta-grounded wye step-up connection
Delta-grounded wye step-down connection

## Slide 47
Delta-Grounded Wye Step-Up Connection
The primary (low side) line-to-line voltages are given by
(39)
where
The primary delta currents are given by
where
(40)

## Slide 48
Delta-Grounded Wye Step-Up Connection
The primary line currents are given by
where
(41)
The forward sweep matrices are
Applying Equation (28),
(42)
Applying Equation (31),
(43)

## Slide 49
Delta-Grounded Wye Step-Up Connection
The backward sweep matrices are
Applying Equation (19),
Applying Equation (23),
(44)
(45)
Applying Equation (37),
(46)

## Slide 50
Undergrounded Wye-Delta Step-Down Connection
Three single-phase transformers can be connected in a wye–delta connection. The neutral of the wye can be grounded or ungrounded. The grounded wye connection is characterized by
The grounded wye provides a path for zero sequence currents for line-to-ground faults upstream from the transformer bank. This causes the transformers to be susceptible to burnouts on the upstream faults.
If one phase of the primary circuit is opened, the transformer bank will continue to provide three-phase service by operating as an open wye–open delta bank. However, the two remaining transformers may be subjected to an overload condition leading to burnout.
The most common connection is the ungrounded wye–delta. This connection is typically used to provide service to a combination of single-phase “lighting” load and a three-phase “power” load such as an induction motor. The generalized constants for the ungrounded wye–delta transformer connection will be developed following the same procedure as was used for the delta–grounded wye.

## Slide 51
Undergrounded Wye-Delta Step-Down Connection
Three single-phase transformers can be connected in an ungrounded-wye “standard 30 degree connection” as shown in Fig.8.
The voltage phasor diagrams in Fig.8 illustrate that the high-side positive sequence line-to-line voltage leads the low-side positive sequence line-to-line voltage by 30°. Also, the same phase shift occurs between the high-side line-to-neutral voltage and the low-side “equivalent” line-to-neutral voltage. The negative sequence phase shift is such that the high-side negative sequence voltage will lag the low-side negative sequence voltage by 30°.
Fig.8 Standard ungrounded wye-delta connection step-down

## Slide 52
Undergrounded Wye-Delta Step-Down Connection
Fig.9 Positive sequence current phasors
The positive sequence current phasor diagrams for the connection in Fig.8 are shown in Fig.9.
Fig.9 illustrates that the positive sequence line current on the high side of the transformer (node n) leads the low-side line current (node m) by 30°. It can also be shown that the negative sequence high-side line current will lag the negative sequence low-side line current by 30°.

## Slide 53
Undergrounded Wye-Delta Step-Down Connection
Fig.9 Positive sequence current phasors
The positive sequence current phasor diagrams for the connection in Fig.8 are shown in Fig.9.
Fig.9 illustrates that the positive sequence line current on the high side of the transformer (node n) leads the low-side line current (node m) by 30°. It can also be shown that the negative sequence high-side line current will lag the negative sequence low-side line current by 30°.
The definition for the “turns ratio nt” will be the same as Equation (9) with the exception that the numerator will be the line-to-neutral voltage and the denominator will be the line-to-line voltage. It should be noted in Fig.8 that the “ideal” low-side transformer voltages for this connection will be line-to-line voltages. Also, the “ideal” low-side currents are the currents flowing inside the delta.

## Slide 54
Undergrounded Wye-Delta Step-Down Connection
The basic “ideal” transformer voltage and current equations as a function of the “turns ratio” are
where
(47)
(48)
(49)
(50)

## Slide 55
Undergrounded Wye-Delta Step-Down Connection
(48)
Solving Equation (48) for the “ideal” delta transformer voltages,
(51)
The line-to-line voltages at node m as a function of the “ideal” transformer voltages and the delta currents are given by
(52)
(53)

## Slide 56
Undergrounded Wye-Delta Step-Down Connection
(51)
(53)
(50)
Substitute Equations (50) and (51) into Equation (53):
(54)
where
(55)
The line currents on the delta side of the transformer bank as a function of the wye transformer currents are given by
(56)
where
(57)

## Slide 57
Undergrounded Wye-Delta Step-Down Connection
(50)
(56)
Substitute Equation (50) into Equation (56):
(58)
where
(59)

## Slide 58
Undergrounded Wye-Delta Step-Down Connection
Because the matrix [DY] is singular, it is not possible to use Equation (58) to develop an equation relating the wye-side line currents at node n to the delta-side line currents at node m. In order to develop the necessary matrix equation, three independent equations must be written. Two independent KCL equations at the vertices of the delta can be used. Because there is no path for the high-side currents to flow to ground, they must sum to zero and, therefore, so must the delta currents in the transformer secondary sum to zero. This provides the third independent equation. The resulting three independent equations in matrix form are given by
(60)
Solving Equation (60) for the delta currents,
(61)
(62)

## Slide 59
Undergrounded Wye-Delta Step-Down Connection
(62)
Equation (62) can be modified to include the phase c current by setting the third column of the [L0] matrix to zero:
(63)
(64)
Solve Equation (50) for [IABC] and substitute into Equation (64):
(50)
(65)
where
(66)

## Slide 60
Undergrounded Wye-Delta Step-Down Connection
(63)
(66)
Equation (66) defines the generalized constant matrix [dt] for the ungrounded wye–delta transformer connection. In the process of the derivation, a very convenient equation (Equation (63)) evolved that can be used anytime the currents in a delta need to be determined knowing the line currents. However, it must be understood that this equation will only work when the delta currents sum to zero, which means an ungrounded neutral on the primary.
The generalized matrices [at] and [bt] can now be developed. Solve Equation (54) for [VLNABC]:
(54)
(67)

## Slide 61
Undergrounded Wye-Delta Step-Down Connection
(67)
(65)
Substitute Equation (65) into Equation (67):
where
where
(68)
(69)
(70)

## Slide 62
Undergrounded Wye-Delta Step-Down Connection
The generalized constant matrices have been developed for computing voltages and currents from the load toward the source (backward sweep). The forward sweep matrices can be developed by referring back to Equation (54), which is repeated here for convenience:
(71)
Equation (16) is used to compute the equivalent line-to-neutral voltages as a function of the line-to-line voltages:
(16)
(72)

## Slide 63
Undergrounded Wye-Delta Step-Down Connection
(71)
(72)
Substitute Equation (71) into Equation (72):
(73)
where
(74)
(75)
The generalized matrices have been developed for the ungrounded wye–delta transformer connection. The derivation has applied basic circuit theory and the basic theories of transformers. The end result of the derivations is to provide an easy method of analyzing the operating characteristics of the transformer connection. Example 8.3 will demonstrate the application of the generalized matrices for this transformer connection.

## Slide 64
Example 3
Fig.10 shows three single-phase transformers in an ungrounded wye–delta connection serving a combination of single-phase and three-phase load in a delta connection. The voltages at the load are balanced three phase of 240 V line to line. The net loading by phase is
Fig.10 Undergrounded wye-delta step-down with unbalanced load

## Slide 65
Example 3
The transformers are rated as follows:
Phase AN: 100 kVA, 7200–240 V, Z = 0.01 + j0.04 per unit
Phases BN and CN: 50 kVA, 7200–240 V, Z = 0.015 + j0.035 per unit
Determine the following:
The currents in the load
The secondary line currents
The equivalent line-to-neutral secondary voltages
The primary line-to-neutral and line-to-line voltages
The primary line currents
Before the analysis can start, the transformer impedances must be converted to actual values in Ohms and located inside the delta-connected secondary windings.
“Lighting” transformer:
“Power” transformers:

## Slide 66
Example 3
The transformer impedance matrix can now be defined:
The turn's ratio of the transformers is = 7200/240 = 30.
Define all of the matrices

## Slide 67
Example 3

## Slide 68
Example 3
Define the line-to-line load voltages:
Define the loads:
kVA
Calculate the delta load current

## Slide 69
Example 3
Compute the secondary line current:
Compute the equivalent secondary line-to-neutral voltages:
Use the generalized constant matrices to compute the primary line-to-neutral voltages and line-to-line voltages:

## Slide 70
Example 3
The high primary line currents are
It is interesting to compute the operating kVA of the three transformers. Taking the product of the transformer voltage times the conjugate of the current gives the operating kVA of each transformer.
The operating power factors of the three transformers are

## Slide 71
Example 3
Note that the operating kVAs do not match very closely the rated kVAs of the three transformers. In particular, the transformer on phase A did not serve the total load of 100 kVA that is directly connected its terminals. That transformer is operating below rated kVA, while the other two transformers are overloaded. In fact, the transformer connected to phase B is operating 35% above rated kVA. Because of this overload, the ratings of the three transformers should be changed so that the phase B and phase C transformers are rated 75 kVA. Finally, the operating power factors of the three transformers bare little resemblance to the load power factors.
Example 3 demonstrates how the generalized constant matrices can be used to determine the operating characteristics of the transformers. In addition, the example shows that the obvious selection of transformer ratings will lead to an overload condition on the two power transformers. The beauty in this is that if the generalized constant matrices have been applied in a computer program, it is a simple task to change the transformer kVA ratings and be assured that none of the transformers will be operating in an overload condition.
Example 3 has demonstrated the “backward” sweep to compute the primary voltages and currents. As before when the source (primary) voltages are given along with the load PQ, then the ladder iterative technique must be used to analyze the transformer connection.

## Slide 72
Undergrounded Wye-Delta Step-up Connection
The connection diagram for the step-up connection is shown in Fig.11.
The only difference between the step-up and step-down connections are the definitions of the turns ratio nt, [AV], and [AI]. For the step-up connection,
Fig.11 Undergrounded wye-delta step-up connection
(76)
(77)
(78)

## Slide 73
Example 5
The equations for the forward and backward sweep matrices, as defined in Section 8.3, can be applied using the definitions in Equations (76) through (78). The system of Example 8.3 is modified so that transformer connection is step-up. The transformers have the same ratings, but now the rated voltages for the primary and secondary are
(76)
(77)
(78)
Primary:
Secondary:

## Slide 74
Example 5
The transformer impedances must be computed in Ohms relative to the secondary and then used to compute the new forward and backward sweep matrices. When this is done the new matrices are
Using these matrices and the same loads, the output of the program gives the new load voltages as

## Slide 75
Grounded Wye-Delta Step-Down Connection
The connection diagram for the standard 30 degree grounded wye (high)–delta (low) transformer connection grounded through an impedance of Zg is shown in Fig.12. Note that the primary is grounded through an impedance Zg.
Basic transformer equations:
The turn's ratio is given by
Fig.12 The grounded wye-delta connection
(79)

## Slide 76
Grounded Wye-Delta Step-Down Connection
Basic transformer equations:
The basic “ideal” transformer voltage and current equations as a function of the turns ratio are
(80)
(81)

## Slide 77
Grounded Wye-Delta Step-Down Connection
(80)
Solving Equation (80) for the “ideal” transformer voltages,
(82)
The line-to-neutral transformer primary voltages as a function of the system line-to-ground voltages are given by
(83)
where

## Slide 78
Grounded Wye-Delta Step-Down Connection
(84)
The line-to-line voltages on the delta side are given by
Substitute Equation (82) into Equation (84):
(82)
(85)
Substitute Equation (81) into Equation (85):
(81)
(86)

## Slide 79
Grounded Wye-Delta Step-Down Connection
(86)
(83)
Substitute Equation (83) into Equation (86):
(87)
Equation (81) gives the delta secondary currents as a function of the primary wye-side line currents. The secondary line currents are related to the secondary delta currents by
(81)
(88)

## Slide 80
Grounded Wye-Delta Step-Down Connection
The real problem of transforming currents from one side to the other occurs for the case when the line currents on the delta secondary side [Iabc] are known and the transformer secondary currents [IDabc] and primary line currents on the wye side [IABC] are needed. The only way a relationship can be developed is to recognize that the sum of the line-to-line voltages on the delta secondary of the transformer bank must add up to zero. Three independent equations can be written as follows:
(89)
KVL around the delta secondary windings gives
(90)
Replacing the “ideal” secondary delta voltages with the primary line-to-neutral voltages,
(91)

## Slide 81
Grounded Wye-Delta Step-Down Connection
(91)
Multiply both sides of the Equation (91) by the turns ratio nt:
(92)
Determine the left side of Equation (92) as a function of the line-to-ground voltages using Equation (83):
(83)
()
(93)
()

## Slide 82
Grounded Wye-Delta Step-Down Connection
(92)
(93)
()
Substitute Equation (93) into Equation (92):
(94)

## Slide 83
Grounded Wye-Delta Step-Down Connection
(94)
(89)
(88)
Equations (88), (89), and (94) can be put into matrix form:
(95)
Equations (95) in general form is
(96)
Solve for
(97)

## Slide 84
Grounded Wye-Delta Step-Down Connection
(97)
Equations (97) in full form is
(98)
Equations (98) in short form is
(99)

## Slide 85
Grounded Wye-Delta Step-Down Connection
(98)
(81)
Substitute Equation (81) into Equation (98):
(100)
where
Equation (100) is used in the “backward” sweep to compute the primary currents based upon the secondary currents and primary LG voltages.

## Slide 86
Grounded Wye-Delta Step-Down Connection
(100)
(87)
The “forward” sweep equation is determined by substituting Equation (100) into Equation (87):
Define
(101)

## Slide 87
Grounded Wye-Delta Step-Down Connection
(101)
The final form of Equation (101) gives the equation for the forward sweep:
where
(102)

## Slide 88
Open Wye-Open Delta
A common load to be served on a distribution feeder is a combination of a single-phase lighting load and a three-phase power load. Many times the three-phase power load will be an induction motor. This combination load can be served by a grounded or ungrounded wye–delta connection as previously described or by an “open wye–open delta” connection. When the three-phase load is small compared to the single-phase load, the open wye–open delta connection is commonly used. The open wye–open delta connection requires only two transformers, but the connection will provide three-phase line-to-line voltages to the combination load. Fig.13 shows the open wye–open delta connection and the primary and secondary positive sequence voltage phasors.
Fig.13 Open wye-open delta connection

## Slide 89
Open Wye-Open Delta
Fig.13 Open wye-open delta connection
With reference to Fig.13, the basic “ideal” transformer voltages as a function of the “turn's ratio” are
(103)

## Slide 90
Open Wye-Open Delta
The currents as a function of the turn's ratio are given by
(104)
Equation (104) can be expressed in matrix form by
(105)
The ideal voltages in the secondary can be determined by
(106)

## Slide 91
Open Wye-Open Delta
(107)
Substitute Equation (106) into Equation (103):
(106)
(103)
Equation (107) can be put into three-phase matrix form as
(108)

## Slide 92
Open Wye-Open Delta
(108)
The secondary line-to-line voltages in Equation (108) can be replaced by the equivalent line-to-neutral secondary voltages:
where
The source-side line currents as a function of the load-side line currents are given by
(109)
(110)

## Slide 93
Open Wye-Open Delta
(109)
(110)
Equations (109) and (110) give the matrix equations for the backward sweep. The forward sweep equation can be determined by solving Equation (107) for the two line-to-line secondary voltages:
(107)
(111)
The third line-to-line voltage Vca must be equal to the negative sum of the other two line-to-line voltages (KVL). In matrix form, the desired equation is
(112)

## Slide 94
Open Wye-Open Delta
(113)
The equivalent secondary line-to-neutral voltages are then given by
The forward sweep equation is given by
where
(114)

## Slide 95
Open Wye-Open Delta
The open wye–open delta connection derived in this section utilized phases A and B on the primary. This is just one of three possible connections. The other two possible connections would use phases B and C and then phases C and A. The generalized matrices will be different from those just derived. The same procedure can be used to derive the matrices for the other two connections.
The terms “leading” and “lagging” connection are also associated with the open wye–open delta connection. When the lighting transformer is connected across the leading of the two phases, the connection is referred to as the “leading” connection. Similarly, when the lighting transformer is connected across the lagging of the two phases, the connection is referred to as the “lagging” connection. For example, if the bank is connected to phases A and B and the lighting transformer is connected from phase A to ground, this would be referred to as the “leading” connection because the voltage A-G leads the voltage B-G by 120°. Reverse the connection and it would now be called the “lagging” connection. Obviously, there is a leading and lagging connection for each of the three possible open wye–open delta connections.

## Slide 96
Grounded Wye- Grounded Wye Connection
The grounded wye–grounded wye connection is primarily used to supply single-phase and three-phase loads on four-wire multigrounded systems. The grounded wye–grounded wye connection is shown in Fig.14.
Fig.14 Grounded wye-grounded wye connection

## Slide 97
Grounded Wye- Grounded Wye Connection
Unlike the delta–wye and wye–delta connections, there is no phase shift between the voltages and the currents on the two sides of the bank. This makes the derivation of the generalized constant matrices much easier. The ideal transformer equations are
(115)
(116)
(117)

## Slide 98
Grounded Wye- Grounded Wye Connection
Fig.14 Grounded wye-grounded wye connection
With reference to Fig.14, the ideal transformer voltages on the secondary windings can be computed by
(118)

## Slide 99
Grounded Wye- Grounded Wye Connection
(118)
(116)
Substitute Equation (118) into Equation (116):
(119)
Equation (119) is the backward sweep equation with the [at] and [bt] matrices defined by
(120)
(121)

## Slide 100
Grounded Wye- Grounded Wye Connection
(119)
The primary line currents as a function of the secondary line currents are given by
where
(122)
The forward sweep equation is determined solving Equation (119) for the secondary line-to-ground voltages:
(123)
The modeling and analysis of the grounded wye–grounded wye connection does not present any problems. Without the phase shift there is a direct relationship between the primary and secondary voltages and currents as had been demonstrated in the derivation of the generalized constant matrices.

## Slide 101
Delta-Delta Connection
Fig.15 Grounded wye-grounded wye connection
The delta–delta connection is primarily used on three-wire delta systems to provide service to a three-phase load or a combination of three-phase and single-phase loads. Three single-phase transformers connected in a delta–delta are shown in Fig.15.

## Slide 102
Delta-Delta Connection
The basic ideal transformer voltage and current equations as a function of the “turn’s ration” are
(124)
(125)
(126)

## Slide 103
Delta-Delta Connection
(126)
Solve Equation (126) for the source-side delta currents:
(127)
The line currents as a function of the delta currents on the source side are given by
(128)
where
Substitute Equation (127) into Equation (128)
(129)

## Slide 104
Delta-Delta Connection
(129)
Since [AI] is a diagonal matrix, Equation (129) can be rewritten as
(130)
The load-side line currents as a function of the load-side delta currents:
(131)
Applying Equation (131), Equation (130) becomes
(132)
Turn Equation (132) around to solve for the load-side line currents as a function of the source-side line currents:
(133)
Equations (132) and (133) merely demonstrate that the line currents on the two sides of the transformer are in phase and differ only by the turn's ratio of the transformer windings. In the per-unit system, the per-unit line currents on the two sides of the transformer are exactly equal.

## Slide 105
Delta-Delta Connection
The ideal delta voltages on the secondary side as a function of the line-to-line voltages, the delta currents, and the transformer impedances are given by
where
(134)
Substitute Equation (134) into Equation (125)
(135)
Solve Equation (135) for the load-side line-to-line voltages:
(136)
The delta currents [IDabc] in Equations (135) and (136) need to be replaced by the secondary line currents [Iabc].

## Slide 106
Delta-Delta Connection
In order to develop the needed relationship, three independent equations are needed. The first two come from applying KCL at two vertices of the delta connected secondary:
(137)
The third equation comes from recognizing that the sum of the primary line-to-line voltages and therefore the secondary ideal transformer voltages must sum to zero. KVL around the delta windings gives
(138)
Replacing the “ideal” delta voltages with the source-side line-to-line voltages,
(139)
Since the sum of the line-to-line voltages must equal zero (KVL) and the turn's ratios of the three transformers are equal, Equation (139) is simplified to
(140)

## Slide 107
Delta-Delta Connection
(140)
Note in Equation (140) that if the three transformer impedances are equal, then the sum of the delta currents will add to zero, meaning that the zero sequence delta currents will be zero.
Equations (137) and (140) can be put into matrix form:
(141)
where

## Slide 108
Delta-Delta Connection
(141)
Solve Equation (141) for the load-side delta currents:
(142)
where
Writing Equation (142) in matrix form gives
(143)
From Equations (142) and (143), it is seen that the delta currents are a function of the transformer impedances and just the line currents in phases a and b. Equation (143) can be modified to include the line current in phase c by setting the last column of the [G] matrix to zeros:
(144)

## Slide 109
Delta-Delta Connection
(144)
(135)
When the impedances of the transformers are equal, the sum of the delta currents will be zero meaning that there is no circulating zero sequence current in the delta windings.
Substitute Equation (144) into Equation (135):
(145)
The generalized matrices are defined in terms of the line-to-neutral voltages on the two sides of the transformer bank. Equation (145) is modified to be in terms of equivalent line-to-neutral voltages:
(146)
Equation (146) is in the general form
(147)

## Slide 110
Delta-Delta Connection
(133)
Equation (133) gives the generalized equation for currents:
(148)
The forward sweep equations can be derived by modifying Equation (136) in terms of equivalent line-to-neutral voltages:
(149)
The forward sweep equation is
(150)
where
The forward and backward sweep matrices for the delta–delta connection have been derived. Once again it has been a long process to get to the final six equations that define the matrices. The derivation provides an excellent exercise in the application of basic transformer theory and circuit theory. Once the matrices have been defined for a particular transformer connection, the analysis of the connection is a relatively simple task. Example 8 will demonstrate the analysis of this connection using the generalized matrices.

## Slide 111
Example 8
Fig.16 shows three single-phase transformers in a delta–delta connection serving an unbalanced three-phase load connected in delta.
The source voltages at the load are balanced three phase of 240 V line to line:
Fig.16 Delta-delta bank serving an unbalanced delta connected load

## Slide 112
Example 8
The loading by phase is
Sab = 100 kVA at 0.9 lagging power factor
Sbc = Sca = 50 kVA at 0.8 lagging power factor
The ratings of the transformers are
Phase AB: 100 kVA, 12,470–240 V, Z = 0.01 + j0.04 per unit
Phases BC and CA 50 kVA, 12,470–240 V, Z = 0.015 + j0.035 per unit
Determine the following:
The load line-to-line voltages
The secondary line currents
The primary line currents
The load currents
Load voltage unbalance
Before the analysis can start, the transformer impedances must be converted to actual values in Ohms and located inside the delta connected secondary windings.
Phase ab transformer:

## Slide 113
Example 8
Phase bc and ca transformers:
The transformer impedance matrix can now be defined
The turn's ratio of the transformers is nt = 12,470/240 = 51.9583.
Define all of the matrices:

## Slide 114
Example 8
=

## Slide 115
Example 8

## Slide 116
Example 8
The Mathcad program is modified slightly to account for the delta connections. The modified program is shown in Fig.17.
Fig.17 Mathcad program

## Slide 117
Example 8
After six iterations, the results are
This example demonstrates that a small change in the Mathcad program can be made to represent the delta–delta transformer connection.

## Slide 118
Open Delta-Open Delta
Fig.18 Open delta-open delta using phases AB and BC
The open delta–open delta transformer connection can be connected in three different ways. Fig.18 shows the connection using phase AB and BC.
The relationship between the primary line-to-line voltages and the secondary ideal voltage is given by
(151)

## Slide 119
Open Delta-Open Delta
The last row of the matrix [AV] is the result that the sum of the line-to-line voltages must be equal to zero.
The relationship between the secondary and primary line currents is
(152)
The primary line currents as a function of the secondary line currents are given by
(153)

## Slide 120
Open Delta-Open Delta
The ideal secondary voltages are given by
(154)
The primary line-to-line voltages as a function of the secondary line-to-line voltages are given by
(155)
The sum of the primary line-to-line voltages must equal zero. Therefore, the voltage VCA is given by
(156)

## Slide 121
Open Delta-Open Delta
(155)
(156)
Equations (155) and (156) can be put into matrix form to create the backward sweep voltage equation:
(157)

## Slide 122
Open Delta-Open Delta
(157)
Equation (157) gives the backward sweep equation in terms of line-to-line voltages. In order to convert the equation to equivalent line-to-neutral voltages, the [W] and [D] matrices are applied to Equation (157):
(158)

## Slide 123
Open Delta-Open Delta
The forward sweep equation can be derived by defining the ideal voltages as a function of the primary line-to-line voltages:
(159.a)
The ideal secondary voltages as a function of the terminal line-to-line voltages are given by
(159.b)

## Slide 124
Open Delta-Open Delta
(159.a)
(159.b)
(158)
Equate Equation (158) to Equation (159):
(160)
Equation (160) gives the forward sweep equation in terms of line-to-line voltages. As before, the [W] and [D] matrices are used to convert Equation (160) using line-to-neutral voltages:
(161)

## Slide 125: Thank You!