## Slide 1: Solving Power Flow Using Bus Injection Model
ECpE Department

## Slide 2: Acknowledgement
[1] Kersting, William H. "Distribution system modeling and analysis." Electric power generation, transmission, and distribution. CRC press, 2018. 26-1.
[2] McCalley, James D. "The Power Flow Problem." https://home.engineering.iastate.edu/~jdm/ee553/PowerFlow.pdf.
[3] Dugan, Roger C., and T. McDermott. "Reference guide." The Open Distribution System Simulator (OpenDSS). EPRI (2016).
[4] "Yprimitive and Ymatrix." YouTube, https://youtu.be/TRfcX6_D3Fw?si=bVURan_lGfx1JuzF.

## Slide 3: 1 Overall Structure of Solving Power Flow
ECpE Department
  This figure illustrates how the OpenDSS puts all the power delivery elements and power conversion elements together to perform a solution.
  Power delivery elements transport energy from one point to another.
    Line, transformer, capacitor and reactor, etc.
  Power conversion elements convert power from electrical form to some other form, or vice versa.
    Load and generator, etc.

## Slide 4: 2 Example 1: Constant-Z Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. Z)
OpenDSS model:
  Clear
  //-------------- Define a new circuit --------------------//
  new circuit.experiment
  //---------------Define a Voltage source------------------//
  Edit "Vsource.source" phases=3 basekv=13.8 Pu=1.02 bus1=K R1=5 X1=0 R0=5 X0=0
  //----------------- Define line codes --------------------//
  New LineCode.Code1 nphases= 3 Units= mi
  ~ Rmatrix= (0.62 | 0.17 0.62 | 0.17 0.17 0.62 )
  ~ Xmatrix= (1.21 | 0.43 1.21 | 0.43 0.43 1.21 )
  New LineCode.Code2 nphases= 3 Units= mi
  ~ Rmatrix= (1.19 | 0.23 1.19 | 0.23 0.23 1.19 )
  ~ Xmatrix= (1.21 | 0.49 1.21 | 0.49 0.49 1.21 )
  … (continued)

## Slide 5: 2 Example 1: Constant-Z Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. Z)
OpenDSS model:
  … (continued)
  //--------------- Define line 1 and 2 ------------------//
  New Line.1 phases=3 Bus1=k.1.2.3 Bus2=m.1.2.3 length=1 units=mi LineCode=Code1
  New Line.2 phases=3 Bus1=m.1.2.3 Bus2=n.1.2.3 length=1 units=mi LineCode=Code2
  //---------------- Define a load -----------------------//
  New Load.L Bus1=n.1.2.3.0 Phases=3 Conn=wye Model=2 kV=13.8 kW=500 kvar=0
  Set VoltageBases = "13.8"
  Solve
Constant-impedance load

## Slide 6: 2 Example 1: Constant-Z Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. Z)
~
~
~
Vsource
Bus k
1
2
3
Bus n
1
2
3
Load (const. Z)
Isource
Bus k
1
→
2
→
3
→
1
→
2
→
3
→
Bus n
Load with compensation current
Thevinen equivalent to Norton equivalent
Various loads to a generic load model (Constant Z + compensation current)
For const. Z, I=0

## Slide 7: 2 Example 1: Constant-Z Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. Z)
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load

## Slide 8: 2 Example 1: Constant-Z Load
ECpE Department
Definitions:
  ,
  ,
  ,
  ,
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 9: 2 Example 1: Constant-Z Load
ECpE Department
(1) Bus k:
1) Branch currents of Vsource:
According to Kirchhoff’s voltage law:
where, , .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 10: 2 Example 1: Constant-Z Load
ECpE Department
(1) Bus k:
2) Branch currents of Line 1:
According to Kirchhoff’s voltage law:
where, , .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 11: 2 Example 1: Constant-Z Load
ECpE Department
(1) Bus k:
Injection currents at Bus k:
where,.
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 12: 2 Example 1: Constant-Z Load
ECpE Department
(2) Bus m:
1) Branch currents of Line 1
According to Kirchhoff’s voltage law:
where, .
Strictly, should be . For a line, , so is used here.
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 13: 2 Example 1: Constant-Z Load
ECpE Department
(2) Bus m:
2) Branch currents of Line 2
According to Kirchhoff’s voltage law:
where, , .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 14: 2 Example 1: Constant-Z Load
ECpE Department
(2) Bus m:
Injection currents at Bus m:
where,.
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 15: 2 Example 1: Constant-Z Load
ECpE Department
(3) Bus n:
1) Branch currents of Line 2
According to Kirchhoff’s voltage law:
where, .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 16: 2 Example 1: Constant-Z Load
ECpE Department
(3) Bus n:
2) Branch currents of Load
According to Kirchhoff’s voltage law:
where, .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 17: 2 Example 1: Constant-Z Load
ECpE Department
(3) Bus n:
Injection currents at Bus n:
where,.
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 18: 2 Example 1: Constant-Z Load
ECpE Department
Put all the injection currents together:
where, , .
Conclusions for constructing Y : (1) ; (2) ; (3)
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 19: 2 Example 1: Constant-Z Load
ECpE Department
Exported primitive admittance matrix of each element from OpenDSS:
Vsource |  |  |  |  |  |  |  |  |  |  | 
0.2 | 0 | 0 | 0 | 0 | 0 | -0.2 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | -0.2 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | -0.2 | 0
-0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0
0 | 0 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0
0 | 0 | 0 | 0 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
Line 1 |  |  |  |  |  |  |  |  |  |  | 
0.4314 | -0.7738 | -0.1235 | 0.1881 | -0.1235 | 0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881
-0.1235 | 0.1881 | 0.4314 | -0.7738 | -0.1235 | 0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881
-0.1235 | 0.1881 | -0.1235 | 0.1881 | 0.4314 | -0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738
-0.4314 | 0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | 0.4314 | -0.7738 | -0.1235 | 0.1881 | -0.1235 | 0.1881
0.1235 | -0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | -0.1235 | 0.1881 | 0.4314 | -0.7738 | -0.1235 | 0.1881
0.1235 | -0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | -0.1235 | 0.1881 | -0.1235 | 0.1881 | 0.4314 | -0.7738
Line 2 |  |  |  |  |  |  |  |  |  |  | 
0.5176 | -0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696
-0.1491 | 0.0696 | 0.5176 | -0.4304 | -0.1491 | 0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696
-0.1491 | 0.0696 | -0.1491 | 0.0696 | 0.5176 | -0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304
-0.5176 | 0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696 | 0.5176 | -0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696
0.1491 | -0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696 | -0.1491 | 0.0696 | 0.5176 | -0.4304 | -0.1491 | 0.0696
0.1491 | -0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696 | 0.5176 | -0.4304
Load |  |  |  |  |  |  |  |  |  |  | 
0.002625 | 0 | 0 | 0 | 0 | 0 | -0.00263 | 0 |  |  |  | 
0 | 0 | 0.002625 | 0 | 0 | 0 | -0.00263 | 0 |  |  |  | 
0 | 0 | 0 | 0 | 0.002625 | 0 | -0.00263 | 0 |  |  |  | 
-0.00263 | 0 | -0.00263 | 0 | -0.00263 | 0 | 0.007877 | 0 |  |  |  | 
G
B
Why the Vsource has 6 rows, while the Load has 4 rows?
In OpenDSS, a 3-phase Vsource is a two-terminal object, and is defined as a voltage source behind an impedance, so it has 6 nodes. In contrast, a 3-phase wye-connected load only has one terminal, and only has 4 nodes, A, B, C and neutral.

## Slide 20: 2 Example 1: Constant-Z Load
ECpE Department
  Put all elements’ Yprim together:
Constructing Y
Vsource |  |  |  |  |  |  |  |  |  |  | 
0.2 | 0 | 0 | 0 | 0 | 0 | -0.2 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | -0.2 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | -0.2 | 0
-0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0
0 | 0 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0
0 | 0 | 0 | 0 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
Line 1 |  |  |  |  |  |  |  |  |  |  | 
0.4314 | -0.7738 | -0.1235 | 0.1881 | -0.1235 | 0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881
-0.1235 | 0.1881 | 0.4314 | -0.7738 | -0.1235 | 0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881
-0.1235 | 0.1881 | -0.1235 | 0.1881 | 0.4314 | -0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738
-0.4314 | 0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | 0.4314 | -0.7738 | -0.1235 | 0.1881 | -0.1235 | 0.1881
0.1235 | -0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | -0.1235 | 0.1881 | 0.4314 | -0.7738 | -0.1235 | 0.1881
0.1235 | -0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | -0.1235 | 0.1881 | -0.1235 | 0.1881 | 0.4314 | -0.7738
Line 2 |  |  |  |  |  |  |  |  |  |  | 
0.5176 | -0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696
-0.1491 | 0.0696 | 0.5176 | -0.4304 | -0.1491 | 0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696
-0.1491 | 0.0696 | -0.1491 | 0.0696 | 0.5176 | -0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304
-0.5176 | 0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696 | 0.5176 | -0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696
0.1491 | -0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696 | -0.1491 | 0.0696 | 0.5176 | -0.4304 | -0.1491 | 0.0696
0.1491 | -0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696 | 0.5176 | -0.4304
Load |  |  |  |  |  |  |  |  |  |  | 
0.002625 | 0 | 0 | 0 | 0 | 0 | -0.00263 | 0 |  |  |  | 
0 | 0 | 0.002625 | 0 | 0 | 0 | -0.00263 | 0 |  |  |  | 
0 | 0 | 0 | 0 | 0.002625 | 0 | -0.00263 | 0 |  |  |  | 
-0.00263 | 0 | -0.00263 | 0 | -0.00263 | 0 | 0.007877 | 0 |  |  |  | 
 | K.1 |  | K.2 |  | K.3 |  | M.1 |  | M.2 |  | M.3 |  | N.1 |  | N.2 |  | N.3 | 
K.1 | 0.6314 | -0.7738 | -0.1235 | 0.1881 | -0.1235 | 0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | 0 | 0 | 0 | 0 | 0 | 0
K.2 | -0.1235 | 0.1881 | 0.6314 | -0.7738 | -0.1235 | 0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | 0 | 0 | 0 | 0 | 0 | 0
K.3 | -0.1235 | 0.1881 | -0.1235 | 0.1881 | 0.6314 | -0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | 0 | 0 | 0 | 0 | 0 | 0
M.1 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | 0.9490 | -1.2042 | -0.2726 | 0.2577 | -0.2726 | 0.2577 | -0.5176 | 0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696
M.2 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | 0.1235 | -0.1881 | -0.2726 | 0.2577 | 0.9490 | -1.2042 | -0.2726 | 0.2577 | 0.1491 | -0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696
M.3 | 0.1235 | -0.1881 | 0.1235 | -0.1881 | -0.4314 | 0.7738 | -0.2726 | 0.2577 | -0.2726 | 0.2577 | 0.9490 | -1.2042 | 0.1491 | -0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304
N.1 | 0 | 0 | 0 | 0 | 0 | 0 | -0.5176 | 0.4304 | 0.1491 | -0.0696 | 0.1491 | -0.0696 | 0.5202 | -0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696
N.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1491 | -0.0696 | -0.5176 | 0.4304 | 0.1491 | -0.0696 | -0.1491 | 0.0696 | 0.5202 | -0.4304 | -0.1491 | 0.0696
N.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1491 | -0.0696 | 0.1491 | -0.0696 | -0.5176 | 0.4304 | -0.1491 | 0.0696 | -0.1491 | 0.0696 | 0.5202 | -0.4304

## Slide 21: 2 Example 1: Constant-Z Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. Z)
Load (const. Z)
As shown in the figure, another constant-Z load is connected to Bus m. Then we can define:
,
Then corresponding modifications is required for Bus m, while analysis for Bus k and Bus n remain unchanged.
In this simple example, the system includes only 3 buses and supplies 1 three-phase load at Bus n. If another three-phase load is connected to Bus m, how can we modify the Y matrix?

## Slide 22: 2 Example 1: Constant-Z Load
ECpE Department
(2) Bus m:
1) Branch currents of Line 1
According to Kirchhoff’s voltage law:
where, .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 23: 2 Example 1: Constant-Z Load
ECpE Department
(2) Bus m:
2) Branch currents of Line 2
According to Kirchhoff’s voltage law:
where, , .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 24: 2 Example 1: Constant-Z Load
ECpE Department
(3) Bus m: (Note that the Load at Bus m is not drawn in the Figure due to limited space, but the load current is marked.
2) Branch currents of Load
According to Kirchhoff’s voltage law:
where, .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 25: 2 Example 1: Constant-Z Load
ECpE Department
(2) Bus m:
Injection currents at Bus m:
where,.
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)

## Slide 26: 2 Example 1: Constant-Z Load
ECpE Department
Finally, put all the injection currents together:
where, , .
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load (const. Z)
Conclusions for constructing Y :
, and . It means the off-diagonal sub-matrices correspond to the negative values of the Y matrices of the power delivery elements connecting bus i and j.
. The diagonal sub-matrices are the sum of Y matrices of all the elements connected to bus i.

## Slide 27: 2 Example 1: Constant-Z Load
ECpE Department
  A general outline of solution of the power flow:
  Step 1: Initialization.
    Calculate the injection currents of the Vsource:
    Calculate the initial nodal voltages using with all other injections currents set to 0:
    Step 2:
    Calculate the injection (compensation) currents for all the power conversion (PC) elements and adding them into the appropriate slot in the current vector to obtain , where, denotes the th iteration.
    Step 3:
    Update voltage vector:
    Step 4:
    Check whether the voltage error exceeds the tolerance. If not, go to Step 2.
Note, regarding the injection currents:
1. does not change in each iteration;
2. The currents for a non-constant-Z injection load will change in each iteration.
3. The currents for a constant-Z load will be zero in each iteration, since there’s no compensate current.

## Slide 28: 2 Example 1: Constant-Z Load
ECpE Department
=
4.9355 | 0.0004 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 4.9274 | -0.0152 | -0.0022 | -0.0053 | -0.0022 | -0.0053 | 4.9119 | -0.0307 | -0.0052 | -0.0116 | -0.0052 | -0.0116
0.0001 | 0.0002 | 4.9355 | 0.0004 | 0.0001 | 0.0002 | -0.0022 | -0.0053 | 4.9274 | -0.0152 | -0.0022 | -0.0053 | -0.0052 | -0.0116 | 4.9119 | -0.0307 | -0.0052 | -0.0116
0.0001 | 0.0002 | 0.0001 | 0.0002 | 4.9355 | 0.0004 | -0.0022 | -0.0053 | -0.0022 | -0.0053 | 4.9274 | -0.0152 | -0.0052 | -0.0116 | -0.0052 | -0.0116 | 4.9119 | -0.0307
4.9274 | -0.0152 | -0.0022 | -0.0053 | -0.0022 | -0.0053 | 5.5428 | 1.1746 | 0.168 | 0.4164 | 0.168 | 0.4164 | 5.5301 | 1.1525 | 0.1674 | 0.4063 | 0.1674 | 0.4063
-0.0022 | -0.0053 | 4.9274 | -0.0152 | -0.0022 | -0.0053 | 0.168 | 0.4164 | 5.5428 | 1.1746 | 0.168 | 0.4164 | 0.1674 | 0.4063 | 5.5301 | 1.1525 | 0.1674 | 0.4063
-0.0022 | -0.0053 | -0.0022 | -0.0053 | 4.9274 | -0.0152 | 0.168 | 0.4164 | 0.168 | 0.4164 | 5.5428 | 1.1746 | 0.1674 | 0.4063 | 0.1674 | 0.4063 | 5.5301 | 1.1525
4.9119 | -0.0307 | -0.0052 | -0.0116 | -0.0052 | -0.0116 | 5.5301 | 1.1525 | 0.1674 | 0.4063 | 0.1674 | 0.4063 | 6.7083 | 2.3318 | 0.3988 | 0.8812 | 0.3988 | 0.8812
-0.0052 | -0.0116 | 4.9119 | -0.0307 | -0.0052 | -0.0116 | 0.1674 | 0.4063 | 5.5301 | 1.1525 | 0.1674 | 0.4063 | 0.3988 | 0.8812 | 6.7083 | 2.3318 | 0.3988 | 0.8812
-0.0052 | -0.0116 | -0.0052 | -0.0116 | 4.9119 | -0.0307 | 0.1674 | 0.4063 | 0.1674 | 0.4063 | 5.5301 | 1.1525 | 0.3988 | 0.8812 | 0.3988 | 0.8812 | 6.7083 | 2.3318
R
X

## Slide 29: 2 Example 1: Constant-Z Load
ECpE Department
Matlab code for solving power flow:
  clear;
  j = sqrt(-1);
  %% Compute the Y matrix of each element
  % Vsource
  Z_k = [5+j*0, 0, 0; 0, 5+j*0, 0; 0, 0, 5+j*0];
  Y_k = inv(Z_k);
  % line 1
  Rmatrix_1 = [0.62, 0.17, 0.17; 0.17, 0.62, 0.17; 0.17, 0.17, 0.62];
  Xmatrix_1 = [1.21, 0.43, 0.43; 0.43, 1.21, 0.43; 0.43, 0.43, 1.21];
  Z_km = Rmatrix_1 * 1 + j * Xmatrix_1 * 1;
  Y_km = inv(Z_km);
  % line 2
  Rmatrix_2 = [1.19, 0.23, 0.23; 0.23, 1.19, 0.23; 0.23, 0.23, 1.19];
  Xmatrix_2 = [1.21, 0.49, 0.49; 0.49, 1.21, 0.49; 0.49, 0.49, 1.21];
  Z_mn = Rmatrix_2 * 1 + j * Xmatrix_2 * 1;
  Y_mn = inv(Z_mn);
  % load
  S_load = 500 + j * 0;
  S_n = [S_load/3; S_load/3; S_load/3];
  V_load_mag = 13.8;
  Z_LN = 1000*V_load_mag^2/conj(S_load);
  Z_n = [Z_LN, 0, 0; 0, Z_LN, 0; 0, 0, Z_LN];
  Y_n = inv(Z_n);
  % system Y matrix
  Y = [Y_k + Y_km, -Y_km, zeros(3,3); ...
  -Y_km, Y_km + Y_mn, -Y_mn; ...
  zeros(3,3), -Y_mn, Y_mn + Y_n];
  %% initialization
  I_source = [(1.02*13800/3^0.5)/5; (1.02*13800/3^0.5)/5 * (-1/2-j*3^0.5/2); (1.02*13800/3^0.5)/5 * (-1/2+j*3^0.5/2)];
  I_0 = zeros(9, 1);
  I_0(1:3, :) = I_source;
  V_0 = Y\I_0; % for a constant impedance load, we do not have to perform iterations
A constant-Z load does not need a compensation current. This is the final voltage vector.

## Slide 30: 2 Example 1: Constant-Z Load
ECpE Department
Result Comparison:
Vk1 | 8021.87 | 0.41
Vk2 | -4010.58 | -6947.34
Vk3 | -4011.28 | 6946.94
Vm1 | 8012.36 | -15.92
Vm2 | -4019.97 | -6930.94
Vm3 | -3992.39 | 6946.87
Vn1 | 7992.16 | -30.95
Vn2 | -4022.89 | -6905.93
Vn3 | -3969.27 | 6936.89
Computed voltages (volts) using Matlab
Node
Real
Imaginary
Vk1 | 8021.87 | 0.00
Vk2 | -4010.94 | -6947.14
Vk3 | -4010.94 | 6947.14
Vm1 | 8012.38 | -15.38
Vm2 | -4019.51 | -6931.23
Vm3 | -3992.87 | 6946.61
Vn1 | 7992.17 | -30.69
Vn2 | -4022.66 | -6906.08
Vn3 | -3969.51 | 6936.77
Exported voltages (volts) from OpenDSS
Node
Real
Imaginary

## Slide 31: 3 Example 2: Constant-PQ Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. PQ)
OpenDSS model:
  Clear
  //-------------- Define a new circuit --------------------//
  new circuit.experiment
  //---------------Define a Voltage source------------------//
  Edit "Vsource.source" phases=3 basekv=13.8 Pu=1.02 bus1=K R1=5 X1=0 R0=5 X0=0
  //----------------- Define line codes --------------------//
  New LineCode.Code1 nphases= 3 Units= mi
  ~ Rmatrix= (0.62 | 0.17 0.62 | 0.17 0.17 0.62 )
  ~ Xmatrix= (1.21 | 0.43 1.21 | 0.43 0.43 1.21 )
  New LineCode.Code2 nphases= 3 Units= mi
  ~ Rmatrix= (1.19 | 0.23 1.19 | 0.23 0.23 1.19 )
  ~ Xmatrix= (1.21 | 0.49 1.21 | 0.49 0.49 1.21 )
  … (continued)

## Slide 32: 3 Example 2: Constant-PQ Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. PQ)
OpenDSS model:
  … (continued)
  //--------------- Define line 1 and 2 ------------------//
  New Line.1 phases=3 Bus1=k.1.2.3 Bus2=m.1.2.3 length=1 units=mi LineCode=Code1
  New Line.2 phases=3 Bus1=m.1.2.3 Bus2=n.1.2.3 length=1 units=mi LineCode=Code2
  //---------------- Define a load -----------------------//
  New Load.L Bus1=n.1.2.3.0 Phases=3 Conn=wye Model=1 kV=13.8 kW=500 kvar=500
  Set VoltageBases = "13.8"
  Solve
Constant-PQ load

## Slide 33: 3 Example 2: Constant-PQ Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. PQ)
~
~
~
Vsource
Bus k
1
2
3
Bus n
1
2
3
Load (const. PQ)
Isource
Bus k
1
→
2
→
3
→
1
→
2
→
3
→
Bus n
Load with compensation current
Thevinen equivalent to Norton equivalent
Various loads to a generic load model (Constant Z + compensation current)

## Slide 34: 2 Example 1: Constant-Z Load
ECpE Department
  A general outline of solution of the power flow:
  Step 1: Initialization.
    Calculate the injection currents of the Vsource:
    Calculate the initial nodal voltages using with all other injections currents set to 0:
    Step 2:
    Calculate the injection (compensation) currents for all the power conversion (PC) elements and adding them into the appropriate slot in the current vector to obtain , where, denotes the th iteration.
    Step 3:
    Update voltage vector:
    Step 4:
    Check whether the voltage error exceeds the tolerance. If not, go to Step 2.
Note, regarding the injection currents:
1. does not change in each iteration;
2. The injection currents for a non-constant-Z load will change in each iteration.

## Slide 35: 3 Example 2: Constant-PQ Load
ECpE Department
~
~
~
Vsource
Bus k
Bus m
Bus n
1
2
3
1
2
3
1
2
3
Line 1
Line 2
Load (const. PQ)
,
,
Vsource
Bus k
Line 1
Bus m
Bus n
Line 2
Load
Updated in each iteration

## Slide 36: 3 Example 2: Constant-PQ Load
ECpE Department
=
4.9352 | 0.0634 | 0.0003 | -0.0001 | 0.0003 | -0.0001 | 4.9119 | 0.0556 | -0.0073 | -0.0035 | -0.0073 | -0.0035 | 4.8812 | 0.055 | -0.0163 | -0.0068 | -0.0163 | -0.0068
0.0003 | -0.0001 | 4.9352 | 0.0634 | 0.0003 | -0.0001 | -0.0073 | -0.0035 | 4.9119 | 0.0556 | -0.0073 | -0.0035 | -0.0163 | -0.0068 | 4.8812 | 0.055 | -0.0163 | -0.0068
0.0003 | -0.0001 | 0.0003 | -0.0001 | 4.9352 | 0.0634 | -0.0073 | -0.0035 | -0.0073 | -0.0035 | 4.9119 | 0.0556 | -0.0163 | -0.0068 | -0.0163 | -0.0068 | 4.8812 | 0.055
4.9119 | 0.0556 | -0.0073 | -0.0035 | -0.0073 | -0.0035 | 5.5076 | 1.2497 | 0.155 | 0.4179 | 0.155 | 0.4179 | 5.4732 | 1.2398 | 0.1446 | 0.4084 | 0.1446 | 0.4084
-0.0073 | -0.0035 | 4.9119 | 0.0556 | -0.0073 | -0.0035 | 0.155 | 0.4179 | 5.5076 | 1.2497 | 0.155 | 0.4179 | 0.1446 | 0.4084 | 5.4732 | 1.2398 | 0.1446 | 0.4084
-0.0073 | -0.0035 | -0.0073 | -0.0035 | 4.9119 | 0.0556 | 0.155 | 0.4179 | 0.155 | 0.4179 | 5.5076 | 1.2497 | 0.1446 | 0.4084 | 0.1446 | 0.4084 | 5.4732 | 1.2398
4.8812 | 0.055 | -0.0163 | -0.0068 | -0.0163 | -0.0068 | 5.4732 | 1.2398 | 0.1446 | 0.4084 | 0.1446 | 0.4084 | 6.6214 | 2.4303 | 0.3614 | 0.8818 | 0.3614 | 0.8818
-0.0163 | -0.0068 | 4.8812 | 0.055 | -0.0163 | -0.0068 | 0.1446 | 0.4084 | 5.4732 | 1.2398 | 0.1446 | 0.4084 | 0.3614 | 0.8818 | 6.6214 | 2.4303 | 0.3614 | 0.8818
-0.0163 | -0.0068 | -0.0163 | -0.0068 | 4.8812 | 0.055 | 0.1446 | 0.4084 | 0.1446 | 0.4084 | 5.4732 | 1.2398 | 0.3614 | 0.8818 | 0.3614 | 0.8818 | 6.6214 | 2.4303
R
X

## Slide 37: 3 Example 2: Constant-PQ Load
ECpE Department
Matlab code for solving power flow:
clear;
j = sqrt(-1);
%% compute the Y matrix of each element
% Vsource
Z_k = [5+j*0, 0, 0; 0, 5+j*0, 0; 0, 0, 5+j*0];
Y_k = inv(Z_k);
% line 1
Rmatrix_1 = [0.62, 0.17, 0.17; 0.17, 0.62, 0.17; 0.17, 0.17, 0.62];
Xmatrix_1 = [1.21, 0.43, 0.43; 0.43, 1.21, 0.43; 0.43, 0.43, 1.21];
Z_km = Rmatrix_1 * 1 + j * Xmatrix_1 * 1;
Y_km = inv(Z_km);
% line 2
Rmatrix_2 = [1.19, 0.23, 0.23; 0.23, 1.19, 0.23; 0.23, 0.23, 1.19];
Xmatrix_2 = [1.21, 0.49, 0.49; 0.49, 1.21, 0.49; 0.49, 0.49, 1.21];
Z_mn = Rmatrix_2 * 1 + j * Xmatrix_2 * 1;
Y_mn = inv(Z_mn);
% load
S_load = 500 + j * 500;
S_n = [S_load/3; S_load/3; S_load/3];
V_load_mag = 13.8;
Z_LN = 1000*V_load_mag^2/conj(S_load);
Z_n = [Z_LN, 0, 0; 0, Z_LN, 0; 0, 0, Z_LN];
Y_n = inv(Z_n);
… (continued)

## Slide 38: 3 Example 2: Constant-PQ Load
ECpE Department
Matlab code for solving power flow:
…(continued)
% system Y matrix
Y = [Y_k + Y_km, -Y_km, zeros(3,3); ...
-Y_km, Y_km + Y_mn, -Y_mn; ...
zeros(3,3), -Y_mn, Y_mn + Y_n];
%% initialization
I_source = [(1.02*13800/3^0.5)/5; (1.02*13800/3^0.5)/5 * (-1/2-j*3^0.5/2); (1.02*13800/3^0.5)/5 * (-1/2+j*3^0.5/2)];
I_0 = zeros(9, 1);
I_0(1:3, :) = I_source;
V_0 = Y\I_0;
V_i = V_0;
I_i = I_0;
V_last = V_0;
%% iteration
for i = 1:10
I_load_inj = - conj(1000*S_n ./ V_i(end-2:end, :)) + Y_n * V_i(end-2:end, :);
I_i(end-2:end, :) = I_load_inj;
V_i = Y\I_i;
end

## Slide 39: 3 Example 2: Constant-PQ Load
ECpE Department
Results:
Vk1 | 8020.78 | 103.35
Vk2 | -3920.89 | -6997.88
Vk3 | -4099.90 | 6894.53
Vm1 | 7995.12 | 96.12
Vm2 | -3914.32 | -6972.04
Vm3 | -4080.80 | 6875.92
Vn1 | 7959.89 | 100.70
Vn2 | -3892.74 | -6943.81
Vn3 | -4067.15 | 6843.12
Computed voltages (volts) using Matlab
Node
Real
Imaginary
Vk1 | 8020.78 | 103.60
Vk2 | -3920.67 | -6998.00
Vk3 | -4100.11 | 6894.40
Vm1 | 7995.13 | 96.29
Vm2 | -3914.18 | -6972.13
Vm3 | -4080.95 | 6875.84
Vn1 | 7959.91 | 100.03
Vn2 | -3893.33 | -6943.50
Vn3 | -4066.59 | 6843.47
Exported voltages (volts) from OpenDSS

## Slide 40: Thank You!