## Slide 1: Economics of Distribution Systems
Dr. Zhaoyu Wang
1113 Coover Hall, Ames, IA
wzy@iastate.edu
ECpE Department

## Slide 2: Economics of Distribution Systems
ECpE Department
Acknowledgement:
The slides are developed based in part on Electric Power and Energy Distribution Systems, Models, Methods and Applications, Subrahmanyan S. Venkata, Anil Pahwa, IEEE Press & Wiley, 2022

## Slide 3: 1. Introduction
Most engineering decisions require the commitment of financial resources. Some of these resources will be spent in the present, and more will be needed for the future. In addition, there could be benefits that accrue on an annual basis.
Example: Consider a utility that decides to install capacitors in a distribution system to improve power factor and reduce losses.
  Costs: money to purchase capacitors and related hardware, and for their installation, and a certain amount of money annually to maintain the capacitors.
  Benefits: reduction in losses.
As expenses take place over different years, we cannot simply add all the costs and all the benefits to obtain the net expenses for the project. This is because the value of money is not constant but decreases from one year to the next.
We need to examine some of the factors that are commonly used in engineering economic analysis and arrive at simple approaches to determine costs and benefits of projects over a period of time.

## Slide 4: 2. Basic Concepts
Interest rate is the rate that is applied to a financial transaction.
The rate can be different, depending on the type of transaction.
For example, if you deposit money in your checking account, you get a very small interest, but if you deposit the money in a certificate of deposit (CD), you will get higher interest. However, you will not be able to use the money that you deposited in a CD until it matures.
Similarly, the interest rate that you have to pay to borrow money to buy a car is very different from the interest rate that you would pay to buy a house.
The rates are different due to risks, flexibility, and other factors related to the transaction.
2.1 Interest Rate
2.2 Inflation
Inflation is the rate at which the price of goods and services increases with time.
Inflation in fact is an integral part of the modern economy. It varies from one year to another and from one country to another. Nobody seems alarmed if inflation stays at a small value, but everyone gets worried if its value becomes very large.
Inflation is a complex phenomenon, and its value at a given time depends on the spending behavior of people, policies of the government, international events, and many other factors.
It is almost impossible to predict inflation for the future years.

## Slide 5: 2. Basic Concepts
Discount rate is the rate that is used by businesses to discount money with time to make financial decisions that span several years. Different businesses use different discount rates based on their specific conditions.
Discount rate are often related to the opportunity cost of investing capital.
Investor perspective: $100 today ≈ $112 in a year → 12% discount rate.
Discount rate is usually much higher than the interest rate that you would get from the bank since it includes risk, cost of capital, government policies, and other business factors.
Generally, the discount rate used for engineering economic analysis does not include the effect of inflation. However, if inflation rates for future years are available, they can be included in the discount rate.
If the discount rate does not include inflation, all the future costs and benefits are represented in real dollars (today's dollar), but if they do include inflation, then all the future monies are represented in inflated or nominal dollars.
It turns out that either way the results are the same. Therefore, most people prefer to leave inflation out to keep things simple.
2.3 Discount Rate

## Slide 6: 2. Basic Concepts
Money loses value with time. The more the investor waits to receive the money, the higher the amount he will expect.
Financial analysis converts all the future financial outlays to a present value by defining the present worth factor or discount factor, given as a function of discount rate (d) and years from present (n):
A discount rate of 12% and n = 1 gives a present worth factor of 0.893, which implies that $100 one year from today will have the present worth of $89.30.
Similarly, n = 5 with the same discount rate gives a present worth factor 0.567, and therefore, $100 five years from today have a present worth of $56.70.
2.4 Time Value of Money
2.5 Annuity
Annuity is a term that defines equal financial outlays that occur at fixed interval of time.
For example, if we take a loan for three years from the bank to buy a car, we will be paying the bank a fixed amount of money every month for the following three years. The amount of payment will depend on the amount of loan and the interest rate.
Similarly, in engineering applications, the same amount of expense or benefit may take place on a yearly basis, such as annual cost of maintaining equipment and annual benefits accrued due to the implementation of a new technology.

## Slide 7: 2. Basic Concepts
An annuity of over years can be converted to the present worth by first finding the present worth of the financial outlay for each year and then summing the present worth,
We have considered that payments for each year are made at the end of the year. Now add and subtract from the right-hand side of this equation and let . Then,
The quantity within the parenthesis is a finite geometric series equal to . Upon substitution and simplification, we get
2.6 Present Worth of Annuity

## Slide 8: 2. Basic Concepts
In some situations, certain quantities will increase at a certain rate annually.
An example of such a quantity is losses in distribution feeders. Since losses are dependent on load, and if the load grows at a certain rate, the losses will also grow annually.
With as the rate of load growth, we get a geometric series,
where is the cost due to losses in year . The present worth of such a series over years with the total cost at the end of the first year equal to is
or
where .
2.7 Present Worth of Geometric Series
Now, the quantity within the parenthesis is . Substituting this in the above expression and simplifying gives

## Slide 9: 3. Selection of Devices: Conductors and Transformers
Economics is one of the major factors in the selection of devices and equipment for distribution systems.
The decision should include the total cost including the capital cost, the operating cost, and the cost of losses over the selected life of the equipment.
Focus of this section: Conductors for distribution feeders and distribution transformer selection.
3.1 Distribution Feeder Conductors
The selection of conductors for design and upgrade of distribution systems is an important part of the planning process.
After taking all the factors into consideration, utilities select four or five conductors to meet their requirement, which is done based on life‐cycle economic analysis and engineering judgment.
Historical factors also play a role in the selection process, i.e., if a company has been using a particular size of conductor, they would want to continue to use that size unless there are compelling reasons not to do so.
Some of the important factors to consider are conductor ampacity, conductor resistance, feeder cost, power cost, energy cost, and load growth.

## Slide 10: 3.1.1 Conductor Economics
Every conductor has a unique cost vs. load characteristic. Thus, for the proper selection of conductors, it is necessary to analyze these characteristics.
Initial installation, annual operation and maintenance, and losses are the three components of the total cost.
Initial installation is a one‐time cost, and it is incurred whenever the line is built. This cost is different for different conductor sizes since heavier hardware is needed for larger conductors, and also the handling cost is higher for larger conductors.
Annual operation and maintenance costs are also higher for lines with larger conductors. This is mainly due to the fact that utilities would spend more money on maintenance of those lines that carry higher load since the failure of these lines would impact a larger number of customers.
The present worth of fixed annual expense of $A/year for operation and maintenance over a period of N years at a discount rate of d can be determined by multiplying it by the present worth factor.

## Slide 11: 3.1.1 Conductor Economics
Unlike transmission systems, the feeders and distribution systems are not transposed. Thus, each phase has a different resistance and reactance value. However, for planning purposes, it is prudent to consider them to be equal to simplify computations.
  Option 1: consider the feeders to be transposed and determine the phase impedance matrix. In the next step, transform the matrix to sequence matrix and use the positive sequence resistance and reactance in the calculations.
  Option 2: consider the feeders to be transposed and determine the phase impedance matrix. In the next step, transform the matrix to sequence matrix and use the positive sequence resistance and reactance in the calculations.

## Slide 12: 3.1.1 Conductor Economics
Losses in the lines, which are a function of the peak load, contribute to the variable part of the cost.
If there were any load growth, this cost would increase every year.
Thus, if the peak load in the first year of operation of the line is P MW, losses due to this load can be computed by first determining the current, which is
where V is the line-to-line voltage in kV, and pf is the power factor.
For an annual loss factor (ratio of average loss to loss at peak load) , the total energy losses in the first year for one mile of a three-phase line with a resistance of r ohms per mile are,
where is a constant for the given values of various quantities.

## Slide 13: 3.1.1 Conductor Economics
Multiplying the previous equation by c (cost of energy in ) gives the cost of losses in mile for the first year.
Now, consider that peak load grows at a rate per year. Therefore, the peak load in the year is given by,
Therefore, losses in the year () with the peak load of and the assumption that all the quantities in are fixed are
Now, if we let

## Slide 14: 3.1.1 Conductor Economics
Losses will grow at a rate of j, while other terms in remain constant.
Escalating quantities calculated using present worth factor from the expression of Present Worth of Geometric Series (as discussed in page 7).
As a variation to this issue, we can consider that the load would grow at a certain rate for the first N years and then remain constant. Such a situation can be very easily included in the calculations by splitting the present worth calculation into two parts:
  First part: Present worth of geometric series for N years with load increasing at m per year.
  Second part: Present worth for remaining years with load set at Nth year's value.
To obtain the total present worth, the cost of a line with a specific size of a conductor, we add the installation cost, the present worth of operation and maintenance, and the present worth of losses and obtain the following expression of the total present worth cost:
where ;

## Slide 15: 3.1.1 Conductor Economics
where ;
CostO&M denotes Operation and maintenance cost in $/year/mile;
, present worth factor for fixed annual O&M cost/year; and
, present worth factor for losses changing yearly with changing load.
Thus, the total present worth as a function of peak load in the first year turns out to be a quadratic function.

## Slide 16: 3.1.1 Conductor Economics
The present worth cost of lines of different conductor sizes, and when the total present worth cost vs. peak load characteristics of different conductors are plotted in the Figure.
An important thing to note is that the plots of different conductors intersect with each other, and thus, for every value of peak load there is a conductor with the least cost.
Hence, the peak load range for which a conductor is the most economical is defined as the economic loading range of that conductor. The economic loading range of Conductor 3 is plotted.
The largest conductor in the set has a lower economic loading limit, but the upper economic loading limit is equal to the thermal loading limit of that conductor.
Figure: Economic characteristics of a set of four conductors.

## Slide 17: 3.1.2 Reach of Feeders
The reach of a feeder built with conductors of a specific size is defined as the distance up to which a certain load can be delivered over the feeder without violating the voltage limits at the end of the feeder. Thus, we define the following reaches:
  Thermal reach of a feeder: the distance up to which the feeder can move power at its thermal loading limit (maximum allowed current) while maintaining the voltage within the specified limits.
  Economic reach of a feeder: the distance up to which the feeder is capable of carrying power equal to that determined by the upper limit of the economical loading range of the selected conductor without violating the voltage limits.
The reach of a feeder with a specific conductor size at a given load is determined by first finding the voltage drop on the feeder for the current corresponding to that load.
Assumption: the load is balanced and all the phases have the same impedance.
The percent voltage drop per mile for a distribution feeder is obtained by dividing the voltage drop by the rated line‐to‐neutral voltage and multiplying the result by 100, i.e.,
where V is the rated line-to-line voltage of the system in kV.

## Slide 18: 3.1.2 Reach of Feeders
If the allowed voltage drop is 𝚫V% , the reach, R, of the feeder is given by
or,
(1)
Figure: Economic characteristics of a set of four conductors.
When I = , the computed reach is the thermal reach, and when I = or current corresponding to power at the upper limit of the economic loading range of the conductor, the reach is called economic reach.
Current at intersection of selected conductor's curve with next higher conductor as shown in the Figure.
This point gives the economic loading limit of the conductor; i.e., the conductor is not economical for use beyond this limit. If a reach higher than the economic reach is desired from a feeder, the feeder has to be derated, or the upper loading limit reduced to keep the voltage drop within the limits.
In distribution system design, it is a recommended practice to keep the reach of all the feeders in a system the same by derating all the conductors in the selected set corresponding to the desired reach.

## Slide 19: 3.1.2 Reach of Feeders
A plot showing variation of reach (R) with peak load (P) for any given conductor and power factor can be obtained using:
Note that reach must be computed using the final peak load on the feeder. For example, if a conductor has a certain peak load in the first year and it increases over the years to the final peak load in year N, the peak load in N must be used for reach calculation.
The Figure shows reach as a function of peak load for four conductors. It is very obvious that reach decreases with increase in peak load.
Figure: Reach at different peak loads for selected conductors.

## Slide 20: 3.1.2 Reach of Feeders
Now, if we desire a common reach for these conductors, we draw a horizontal straight line at the desired reach value, which is Rc miles in this figure.
Intersections of the horizontal line at Rc with the reach characteristic of different conductors provide the maximum peak load of the respective conductors for the desired reach.
Therefore, the maximum peak load for a common reach of Rc miles is Pmax1 for Conductor 1, Pmax2 for Conductor 2, Pmax3 for Conductor 3, and Pmax4 for Conductor 4.
Figure: Reach at different peak loads for selected conductors.

## Slide 21: 3.1.2 Reach of Feeders
Now, we use the maximum peak load values obtained from Figure(a) and derate the conductors for a reach of Rc miles to get the revised cost characteristics as shown in Figure(b).
Since the cost characteristics are based on the peak load in the first year, the maximum peak load values from Figure(a) must be scaled down to the first year. For example, the maximum first‐year peak load for Conductor 1 will be
Figure(a): Reach at different peak loads for selected conductors.
Figure(b): Economic cost characteristics of a set of four selected conductors with a common reach of Rc miles.

## Slide 22: 3.1.2 Reach of Feeders
Similarly, we can obtain values of P2, P3, and P4. Because we are derating the conductors, the cost characteristics do not intersect each other any longer.
Therefore, we see a jump from one conductor to the next at the peak loads P1, P2, P3, and P4.
Although the most economical characteristics are those given by the graphs of different conductors in a conductor set, a straight line can be a simple linear approximation for these characteristics.
This line could be a line tangent to the smallest and the largest conductor as shown in Figure(b). Note that the full graph of the largest conductor is not shown in this figure, but the straight‐line approximation does meet its graph at higher values of peak load.
Figure(b): Economic cost characteristics of a set of four selected conductors with a common reach of Rc miles.
Figure(a): Reach at different peak loads for selected conductors.

## Slide 23: 3.1.2 Reach of Feeders
Calculations shown in this section, as well as in the previous section, are for three‐phase feeders. The analysis can be modified for single‐ or two‐phase feeders.
Such modifications are important because a large percentage of feeders in a distribution system carry load below 1 MW, and often, these feeders are single‐phase laterals.
Further, the voltage drop calculations were done with an assumption that the power flowing on the feeder remains the same at the beginning and end of the feeder. But in reality, the power flow decreases as we move along the feeder because the feeder will have laterals tapped off of it to supply loads. This in turn decreases the voltage drop or increases the reach of the feeder.
A factor to account for the reduction in voltage drop for such phenomenon can be included in the calculations. Specifically, a precise value of this factor can be determined if the feeder serves a uniformly distributed load in a rectangular or triangular service area.
However, in reality, these conditions do not exist. So computing a factor to account for reduction in voltage drop is difficult. On the other hand, it is alright if we do not consider this factor because, in emergencies, the feeders may be required to support the additional load of an adjoining feeder. The extra load and reach margin available on the feeders would be valuable in such situations.

## Slide 24: 3.1.3 Optimal Selection of Conductors for Feeders
Selection of a good conductor set is very important for proper planning of distribution systems.
An ideal conductor set should have roughly equal economic loading range for each conductor, sufficient thermal capacity in the largest conductor to take care of situations with very high load, and should be the most optimal in terms of cost.
Generally, it is very difficult to select a conductor set that will meet all the criteria of an ideal set. Most utilities choose conductors for their system based on experience and historical applications.
Usually, the number of conductors in a set is limited to four or five for proper management of inventory. Some authors have addressed this issue to provide a systematic procedure for selection of a good conductor set.
An approach to determine the optimal conductor is by minimizing the aggregate area under the plots of different conductor sets between the minimum and the maximum loads.
For example, in the Figure on page 15, we would integrate from zero to the maximum value of annual peak load on the graph of the lowest cost characteristics considered for different load ranges. The conductor set with minimum value for this area would have an average minimum cost over the whole range of loading.

## Slide 25: 3.1.3 Optimal Selection of Conductors for Feeders
A simpler approach is to compute the area enclosed by the conductor curves and the tangent line to the smallest and the largest conductors in the set as shown in Figure(b), page 20. We call this line the ideal line.
Also, the conductor characteristics shown in this figure account for derating of conductors to accommodate the selected feeder reach.
During various studies we found that none of the conductors had plots that would go below the tangent line. Hence, minimizing the total area under the curves is equivalent to minimizing the area between the curves and the ideal line.
The equation of the ideal line can be obtained by finding the two points where the ideal line would touch the smallest and the largest conductors in the set. These two points are given by the following equations:
and;
  where and are the equations of the smallest and the largest conductors in the set. Let the ideal straight line be:
  ;
  where m is the slop and c is the intercept on the y-axis.

## Slide 26: 3.1.3 Optimal Selection of Conductors for Feeders
However, instead of using this area for the selection of the optimal conductor set, a better approach is to give different weights to areas in different loading ranges, since in most distribution systems a large percentage of feeders carry very small load, and a few feeders carry large load.
For example, in a system discussed in [1], out of 24 800 miles of primary voltage line, close to 56% of the total length of feeders carry power less than 0.5 MW. Around 11% of the total length of feeders carry power between 0.5 and 1 MW. Similar information is given for every increment of 0.5 MW.
Of these feeders, the ones that carry less than 1 MW are usually single‐phase laterals, and the remaining are three‐phase feeders. This shows that two‐thirds of the feeders in a distribution system are single‐phase feeders.
These numbers are for an example system and will be somewhat different for different systems. A utility can very easily obtain such information from their existing system.
[1] Willis, H.L. (1997). Power Distribution Planning Reference Book. New York: Marcel Dekker, Inc.

## Slide 27: 3.1.3 Optimal Selection of Conductors for Feeders
The table shows the percent of the total feeder length with the given peak load in an example distribution system in [1].
The modification included adjusting the percentage for each range to make the sum of the percentages equal 100.
This table includes single‐phase laterals, it must be modified to determine weights to compute the weighted average deviation (WAD).
Consider that a very small percentage of three‐phase feeders will carry peak load below 1 MW, we can discard the first two rows and scale up the percentages for the rest of the rows such that their sum is equal to 100.
Following that, the WAD of the cost of a conductor set from the tangent line can be computed as follows:
To explain this further, let P1 = 1.6 MW and P2 = 2.4 MW. Now, we want to compute the weighted area between Conductor 2 and the ideal line. Since the weights are given for 0.5 MW ranges, we divide the range of integration in 0.5 MW increments. Therefore, the weighted area between Conductor 2 and the ideal line is given by:
The characteristics of Conductor 2 are given by y2 = a2 + b2x2, where w2 is the weight for the loading range from 1.5 to 2 MW, and w3 is the weight for the loading range from 2.0 to 2.5 MW.
The process is repeated for all the conductors in their respective loading ranges up to the maximum load of the largest conductor for the selected reach to determine the WAD.
[1] Willis, H.L. (1997). Power Distribution Planning Reference Book. New York: Marcel Dekker, Inc.
Table: Percentage of conductors with different loading ranges in an example distribution system.

## Slide 28: 3.1.4 Example
In this example, 17 conductors spanning from conductor #1 to 795 kcmil are considered for a 12.47‐kV distribution system. The discount rate is 8%, the load growth rate is 0.5% over a period of 30 years, the loss factor is 0.46, the power factor is 0.9, the cost of energy is 3 cents/kWh, and the planning horizon is 30 years. The smallest and the largest conductors are preselected to be #1 and 795 kcmil, respectively, and the remaining two or three conductors are determined using the procedure described in the previous section. In Method A, the reach of the conductors is not considered for determining the optimal conductor set, and in Method B, a reach of 4.7 miles and allowed voltage drop of 7.5% are considered. The results for a four‐conductor set and a five‐conductor set are given in the Table.
Now, we want to compare the selected sets for a reach of 4.7 miles. To be able to do so, we have to derate the conductors determined with Method A appropriately. The adjusted average‐weighted deviations of the two conductor sets from the ideal cost characteristics are $17 049/mile and $15 160/mile, respectively, for the four‐conductor sets. Thus, the latter conductor set offers an average saving of $1889/mile for a reach of 4.7 miles. Similar analysis for the five‐conductor set gives WAD of $13 471/mile with Method A and $12 691/mile with Method B, thus yielding an average savings of $780/mile.
Table: Best conductor sets.

## Slide 29: 3.1.4 Example
When the common reach was changed to 3.6 miles, the same conductor set #1, 266, 477, and 795 kcmil were found to be the best whether Method A or Method B was used. This is a very interesting result, which can be explained as follows:
  We already know that to increase the reach of a conductor higher than its economic reach, the conductors need to be derated to carry maximum load lower than its economic loading limit. Thus, when the common reach is fixed at 4.7 miles after selecting the conductors, the conductors get derated significantly.
  This is because of the fact that the economic reaches of these conductors vary from 3.1 to 4.7 miles. So, when the reaches of all the conductors are adjusted to be 4.7 miles, all except one of them (266 kcmil, which has the economic reach of 4.7 miles) get derated by a large value.
  But when the reach is fixed at 3.6 miles, the conductors are not derated by a big margin, which implies a smaller deviation from the already selected characteristics. Hence, for smaller reach, the results are the same whether Method A or Method B is used.
  Also, the average weighted deviation from the straight line for a reach of 3.6 miles for the four‐conductor set turned out to be $10 633/mile, which is lower than that for a reach of 4.7 miles.
  This can again be explained by the fact that for a lower reach, derating of the conductors is lower than that for higher reach. Also, the optimal conductor set was found to be the same using both methods for the five‐conductor set, giving a WAD of $9317/mile.

## Slide 30: 3.1.4 Example
The results show that Method B is better than Method A if reach is known ahead of time. But both methods give the same result for shorter reaches.
However, another question that needs to be answered is whether it is better to select five or four conductors. Five‐conductor set offers savings of $2468 over a four‐conductor set for a common reach of 4.7 miles. It offers savings of $1316/mile for a common reach of 3.6 miles. These savings can be very significant, since distribution systems are very extensive and cover large areas.
However, extra cost associated with maintaining an inventory of five conductors in comparison to four conductors has to be considered while making decisions to stock four or five standard conductors in the inventory.

## Slide 31: 3.2 Economic Evaluation of Transformers
Similar to conductors, transformers have to be selected while considering both the capital cost and the operating cost.
We use the economic principles presented in the previous section to determine the best size of the transformer.
Transformer cost elements: Capital cost (Cc), Annual charge rate (Ar, which is inverse of the present worth factor), Annual operating expenses (OPEX).
The expression for the total annual cost () of the transformer is given by,
The annual operating cost includes the cost due to the exciting current , core losses , and copper losses . Therefore,
These costs can be estimated as follows:
  where is the per-unit exciting current of the transformer, kVA is the name plate rating of the transformer, and is the installed cost per kVAr of the primary shunt capacitors.

## Slide 32: 3.2 Economic Evaluation of Transformers
In other words, we are computing the cost of the capacitors needed to compensate the inductance caused by the exciting current in the transformer.
  where is the cost of the investment per load, is the cost of energy generation per are core losses of the transformer in , and are the number of hours/year or 8760 hours.
  where is the incremental cost of the peak generation per kWh, is the loss factor in pu, is the peak load of the transformer in pu, and are the copper loasses of the transformer at the rated load.
Note that the cost of the core losses is treated differently than the cost of the copper losses.
The core losses are constant at all loads, but the copper losses increase with increasing load.
The index of the transformer is defined as:
Economic Performance Index

## Slide 33: 3.2 Economic Evaluation of Transformers
Example
For a 100‐kVA pad mount transformer, the data are given in theTable. Compute the total annual cost and the economic performance index of the transformer.
Solution
Total Annual cost: ACT = 3000 × 0.25 + 498.39 = $1248.39
Economic Performance Index = 1248.39/100 = $12.48/kVA
Table: Data for a 100‐kVA pad mount transformer.

## Slide 34: 4. Tariffs and Pricing
Unlike the transmission systems, which are regulated by the Federal Energy Regulatory Commission, distribution systems are regulated at the state levels.
Electric distribution utilities have an obligation to serve all the customers in their service territory while maintaining a certain level of reliability.
The utilities build, upgrade, and maintain the system to fulfill the obligation. The state corporation commissions allow utilities to include some of these expenses into the rate base.
In other words, the utilities recoup these expenses over time through revenues collected through bills.
Every state has a different model, but there are many common elements to the electricity bills, and we will explore them in this section.

## Slide 35: 4.1 Electricity Rates
4.1.1 Energy
Energy consumed by customers is measured in kilowatt‐hours (kWh) by a meter installed at the service entrance.
The simplest form of rate charges for energy at a fixed rate irrespective of the time when it was consumed.
For customers with large requirements, some utilities have block rates in which the first block of energy consumed has a rate and the next block of energy has a lower or higher rate. Subsequent blocks have lower or higher rates.
4.1.2 Demand
Demand is defined as the largest power demand (kW) measured for a specified duration during the billing period.
For example, customers on a typical demand rate will pay for the energy consumed over the month and will also pay for the maximum one‐hour demand during the month.
The demand can be applicable for all the months or for certain months of the year.

## Slide 36: 4.1 Electricity Rates
4.1.3 Time of Use (TOU)
As the name implies, under this plan varying electricity rates for different blocks of time are usually defined for a 24‐hour day.
TOU rates generally reflect the average cost of generating and delivering power during those time periods.
TOU rates often vary with the time of the day and by the season, which are typically predetermined by the utilities.
This type of pricing requires meters that register cumulative usage during different time blocks. As an example, the utility can define 2:00 p.m. to 7:00 p.m. as the peak period with a higher rate for electricity.
The rate for the off‐peak hours is lower than the flat rate to provide incentive to customers to sign up for this rate plan.
In addition to the peak period, some utilities use three blocks of rates. These blocks are peak, shoulder, and off‐peak. Thus, the off‐peak period could be from 10:00 p.m. to 10:00 a.m., shoulder period from 10:00 a.m. to 2:00 p.m. and from 7:00 p.m. to 10:00 p.m., and peak period from 2:00 p.m. to 7:00 p.m.
In certain cases, the TOU rates are applied only during the summer months.
There are multiple combinations for time of use rates. Some utilities have implemented TOU rates and some have experimented with them, but they are not used very widely in the utility business.

## Slide 37: 4.1 Electricity Rates
4.1.4 Critical Peak Pricing (CPP)
This type of pricing includes a prespecified high rate for usage during periods designated by the utility to be the critical periods.
The CPP events are generally triggered by system contingencies or high prices faced by the utility in procuring power in the wholesale market.
CPP rates may be superimposed on either a TOU or time‐invariant rate and are called on a relatively short notice for a limited number of days or hours per year.
CPP customers typically receive a price discount during non‐CPP periods.
CPP rates have been tested in pilots for large and small customers in several states. While they have not been implemented at a wide scale, they are available to certain class of customers in some areas.

## Slide 38: 4.1 Electricity Rates
Under this plan, the utilities give a predetermined amount of refund to the customers for reducing their consumption when they observe or anticipate high wholesale market prices or power system emergency conditions.
The utilities may call critical events during prespecified time periods (e.g. 3 p.m. to 6 p.m. summer weekday afternoons).
Although the price for electricity during these time periods remains the same, the customer is refunded for any reduction in consumption relative to what the customer was expected to consume.
4.1.5 Critical Peak Rebates (CPRs)
4.1.6 Interruptible Rates
These rates are available to large industrial, commercial, or government customers.
Those under this plan agree to curtail their load by a certain percent under declared emergencies.

## Slide 39: 4.1 Electricity Rates
Since lower power factor results in higher current for the same amount of real power, some utilities charge large customers a penalty for low power factor.
For example, the utility may require the customer to maintain the power factor between 0.95 lagging and unity. Deviations outside of that are assessed a penalty.
4.1.7 Power Factor-Based Rates
4.1.8 Real – Time Price
Real‐time price is commonly used in bulk power systems. For example, power pools such as Southwest Power Pool have the price of electricity in its systems declared every 5 minutes in real time.
Such implementation has not been done in distribution systems. However, in the future, the FERC Order 2222 will allow third‐party aggregators to pool resources from customers in distribution systems and bid in the market.
The resources would be in the form of customer‐owned solar or other generation and reductions in customers load in response to price changes.

## Slide 40: 4.1 Electricity Rates
Net metering is an idea that came into existence to address issues arising from individual customers owning their own generation, such as rooftop solar photovoltaic generation, and injecting the excess power generation into the grid.
In the early days, the utilities compensated the customers at the same rate at which they were selling it to the customers. However, this arrangement was flawed because the rate that utilities charge includes not only the cost of generation but also the cost of delivery.
In addition, the utility has invested in the infrastructure to deliver electricity to customers while maintaining a certain level of expected reliability.
In this arrangement, they are not able to recover money for their investments. Hence, the new net metering rates in place compensate customers at the wholesale rate for electricity in the market. The compensation for a given month is credited in the same month or carried forward to the next month.
Accounting for the load offset behind the meter by local generation is done in different ways:
  Some utilities may consider compensation for it at the full rate, while others may have a reduced rate.
  Some states are allowing utilities to charge a monthly fee in dollars per kW based on the capacity of the customer‐owned system.
This is a complex and controversial subject with many variations, and it is still evolving. With increased number of homes owning their own generation and participating in the market through aggregators, net metering will evolve further.
4.1.9 Net Metering

## Slide 41: 4.2 Understanding Electricity Bills
The rates that a utility charges to its customers are approved by the state regulators of the state in which the utility provides services.
Therefore, each utility has its own schedule of rates, and thus, no two utilities are identical in this regard even within the same state.
While it is not possible to cover all possible billing options, we show an example of a typical utility bill based on the rates for residential customers given in the Table for a large utility company.
Table: Example of rate schedule for residential customers.

## Slide 42: 4.2 Understanding Electricity Bills
Example
Consider that a customer consumes 1125 kWh in the month of July. This customer has purchased RECs to buy electricity from solar facilities. Compute the monthly bill for this customer based on the rate schedule given in Table. The customer has also volunteered to purchase 500 kWh of electricity per month from solar resources and pay a surcharge of 2.055¢ per kWh. In addition to kWh usage, the utility has determined a fuel charge of $21.65 and taxes of $6.13.
Since the month is July, we use the schedule to compute the cost for distribution and energy supply.
Distribution:
Generation:
Transmission:
Green Power:
Monthly Bill
Therefore, the average cost of electricity for this customer is 113.08/1125 = 10.051¢ per kWh.
Table: Example of rate schedule for residential customers.

## Slide 43: 4. Tariffs and Pricing
United States is a large country with many rural communities. Since investor‐owned utilities were not catering to the needs of the rural communities, the government passed legislation in 1936, which resulted in the formation of RECs.
The RECs are member‐owned nonprofit organizations that provide electricity to rural communities.
Large RECs own their own generation and transmission, but smaller ones only engage in the distribution business.
4.3 Rural Electric Cooperatives (RECs)
4.4 Municipal Utilities
Several small cities in the United States operate their own distribution system.
Some of them own small generation within the city limits, but many of them buy electricity from the market to serve their customers.
Since individual cities do not have large market power, typically several cities cooperate to form power purchase pools for better rates.

## Slide 44: Thank You!