## Slide 1: Distribution System Analysis
Dr. Zhaoyu Wang
1113 Coover Hall, Ames, IA
wzy@iastate.edu
ECpE Department

## Slide 2: Distribution System Analysis
ECpE Department
Acknowledgement:
The slides are developed based in part on Electric Power and Energy Distribution Systems, Models, Methods and Applications, Subrahmanyan S. Venkata, Anil Pahwa, IEEE Press & Wiley, 2022

## Slide 3: 1. Introduction
The objective of distribution system analysis is to determine the state of the system including voltages, real and reactive power flow on lines, and losses in the system.
This requires modeling all the components in the system such as lines and transformers and their interconnections based on the topology. In addition, models for loads and sources connected to the system are needed.
Since distribution system is connected to transmission systems, which are connected to large generators, we model the whole upper level system at the point of coupling as an equivalent source.
Distributed energy resources (DERs) directly connected to the distribution system are modeled based on their characteristics.

## Slide 4: 2. Modeling of Source Impedance
A method that is valid for both radial and loop systems is to derive the sequence impedance values from the results of a fault study.
The procedure involves considering different types of faults at the bus of interest and using the equivalent circuit for each fault to determine the source impedance for positive, negative, and zero sequences, as given below for bus m.
Subscripts 1,2,and 0 represents positive, negative and zero sequence quantities

## Slide 5: 2. Modeling of Source Impedance
Where
, system nominal voltage (line neutral);
, three-phase fault current at bus
, line-to-line fault current at bus
, SLG fault current at bus , fault impedance
This method requires the presence of all three phases, as well as line-to-line and single-line-to-ground faults, so it can only be used on buses with all three phases.

## Slide 6: 2. Modeling of Source Impedance
Knowing the sequence values, the corresponding values in the phase domain can be obtained by the proper symmetrical component similarity transformation.
However, the obtained result will be an approximation because all the lines must be fully transposed to balance the three phases for decoupling of the sequence impedances.
This assumption works well in transmission systems but not for distribution systems. So, if we have to represent the entire transmission system at the substation, this approach will work well.

## Slide 7: Approximate Line Segment Model
ECpE Department
The approximate line model can be developed by applying the “reverse impedance transformation” from symmetrical component theory.
Using the known positive and zero sequence impedances, the “sequence impedance matrix” is given by (See Chapter 4, Kersting)
(47)
Note that this assumption means lines are assumed to be transposed, that is why this model is called “approximate” model.
The “reverse impedance transformation” results in the following approximate phase impedance matrix:
(48)
(49)

## Slide 8: 2. Modeling of Source Impedance
For loop systems, if matrix of the entire system in phase domain is known, the diagonal submatrix corresponding to bus is the source impedance matrix. This is also called the driving point impedance matrix.
Note: the driving point impedance obtained based on the positive‐sequence network topology of the system should not be used for fault calculations because it does not account for transformer connections that are important for the zero‐sequence network.

## Slide 9: 3. Load Models
Under steady state, complex power S at any location in a distribution system varies with voltage and can be described as a function of voltage V at that point, that is
Different modeling approaches are used to describe the relationship of the above equation.

## Slide 10: 3. Load Models
3.1 Load Model I
It is usual to represent both P and Q as a general polynomial function of V.
Such a representation is valid for individual type of loads or aggregate (composite) type of loads.
Different conditions for the coefficients give different models. For example:
  If only and are nonzero, and all the coefficients are zero, then,
  and (Constant Power Load)

## Slide 11: 3. Load Models
  If only and are nonzero, and all the coefficients are zero, then,
  and (Constant Current Load)
  If only and are nonzero, and all the coefficients are zero, then,
  and (Constant Impedance Load)

## Slide 12: 3. Load Models
If a load is a combination of the three above mentioned types, we can combine them to find a composite expression. For examples, tests and subsequent regression analysis on the data show the following models for common load types:
(a) Air‐conditioning load demand (per‐unit values):
(b) Fluorescent lighting:
(c) Induction motor:

## Slide 13: 3. Load Models
3.2 Load Model II
Composite loads, which are assumed to be mixtures of the types as discussed, can be represented as:
where both k and l vary between 0 and 3, Vn is the initial or base value of voltage, Pn is the initial or base value of real power, and Qn is the initial or base value of reactive power. When using these models, we should be aware of the range of V for the models to be valid.

## Slide 14: 3. Load Models
3.2 Load Model II
Some examples of using Load Model II:
(a) If k = 1 and l = 0, it implies that the load is a constant current type with unity power factor.
(b) If k = l = 2, the load is a constant impedance type.
(c) If k = 2.5 and l = 2.7, it represents an aluminum reduction plant. This is a simple model and can be determined empirically from measurements.

## Slide 15: 3. Load Models
3.3 Load Model III
If loads (or demands) are sensitive to frequency, the frequency effects should be included. In that case, voltage and frequency dependence are described by the following relationships:
where is the base frequency, and and are constant exponents.

## Slide 16: 3. Load Models
3.3 Load Model III
Instead of determining the exponent for this model, it is often a practice to determine the four sensitivity coefficients. Knowing these coefficients, the new values for ΔP and ΔQ can be determined from Δf and ΔV. All the changes are assumed to be small, thus:

## Slide 17: 3. Load Models
3.3 Load Model III
The table shows the sensitivities coefficients based on the results of a data survey conducted by Electric Power Research Institute (EPRI). The values have been normalized to apparent power, S.
Then, P = Pn + ΔP and Q = Qn + ΔQ for f = fn + Δf and V = Vn + ΔV
Table: Suggested values of sensitivities of real power and reactive power to voltage and frequency changes based on load survey results.

## Slide 18: 3. Load Models
3.4 Load Model IV
The model is particularly suitable for modeling uncertainties in aggregate loads at a node knowing the demand profiles for a day, a season, or a year.
Assuming Gaussian distribution for load demand:
, and
where, 𝑃_𝑝 is the power value at which the probability of load exceeding that value is p%, 𝑘_𝑝 is the coefficient related to p, and σ is the standard deviation of the load.
Typically, p of 10% is used in voltage‐drop calculations, and p of 50% or mean values of load are used for loss calculations. Smaller values of p are used for overload and determination of emergency conditions.

## Slide 19: 4. Distributed Energy Resources (DERs)
Traditional distribution systems were not designed to accommodate active generation and storage. However, with decreasing cost and advances in technology, such devices are being deployed in distribution systems.
DERs are defined as sources of electric power that are not directly connected to the bulk power system but are connected to the distribution system, limited in size to 10 MVA or less.
DER includes generators of different types and energy storage devices with the ability to inject power into the system.

## Slide 20: 4. Distributed Energy Resources (DERs)
Generators include rotating induction or synchronous rotating machines driven by burning diesel, natural gas, bio gas, propane, or by wind or water flow. The static types of DERs include solar photovoltaic (PV) and batteries.
The majority of DERs are connected to the system through a power electronic interface:
  For the resources that generate AC power, the converter changes it to DC power, and an inverter changes it back to AC power at the system frequency.
  For the resources that produce DC power, the inverter changes it to AC power at the system frequency.
The DERs that use a power electronics controller with embedded inverters are called inverter‐based resources (IBRs).

## Slide 21: 4. Distributed Energy Resources (DERs)
Impacts of DERs on Voltage Regulation
Addition of DERs can impact voltage in distribution systems.
Previously, DERs were not permitted to actively regulate voltage. They operated at a fixed power factor.
IEEE 1547 standard revised in 2018 permits DERs to regulate voltage by injecting reactive power.

## Slide 22: 4. Distributed Energy Resources (DERs)
Impacts of DERs on Voltage Regulation
DERs are divided into Category A and Category B.
  Category A for the systems with lower penetration of DERs.
  Category B for the systems with higher penetration of DERs or system with frequent large variations in power output.
The required reactive power capabilities of the DERs for Category A and Category B are shown in the Figure. These requirements apply to DERs for continuous operation when the voltage is 0.88 and 1.1 times the nominal voltage.
Fig: Minimum reactive power capability of Category A and B DER.

## Slide 23: 4. Distributed Energy Resources (DERs)
Control Function Requirements for DERs
Although constant power factor mode with unity power factor setting is the default mode for DER operation unless otherwise specified by the distribution system operator, the distribution system operator has to approve active participation of DERs in voltage regulation.
The 1547 standard requires DERs to have the ability to control voltage, reactive power, and real power within the operating region. These control function requirements are specified in the Table.
Table: Voltage, reactive power, and real power control function requirements for DER

## Slide 24: 4. Distributed Energy Resources (DERs)
Control Function Requirements for DERs
Control modes are illustrated in the figures as per the IEEE Standard 1547.
Fig: Volt-VAr characteristic for DER control

## Slide 25: 4. Distributed Energy Resources (DERs)
Control Function Requirements for DERs
Control modes are illustrated in the figures as per the IEEE Standard 1547.
Fig: Watt-VAr characteristic for DER control

## Slide 26: 4. Distributed Energy Resources (DERs)
Control Function Requirements for DERs
Control modes are illustrated in the figures as per the IEEE Standard 1547.
Fig: Volt–Watt characteristic for DER control.

## Slide 27: 4. Distributed Energy Resources (DERs)
Control Function Requirements for DERs
Standard 1547 provides suggested values for various set points shown in these figures.
The DERs will provide the capabilities of mutually exclusive reactive power control modes listed in this table and will be capable of initiating any of these modes one at a time.

## Slide 28: 4. Distributed Energy Resources (DERs)
Control Function Requirements for DERs
DER operator is responsible for implementing changes to settings and mode selections upon request by the system operator within a specified time. Other control modes mutually agreeable to the DER operator and the system operator can also be implemented.
Irrespective of the type of DER and the selected control mode, DERs supply real power and either supply or absorb reactive power.
Thus, while considering DER as a load, one must consider its real power and reactive power as negative if delivering it, and positive if absorbing it.

## Slide 29: 5. Power Flow Studies
Since a typical distribution system is unbalanced due to both design and operation, it is imperative that the system's steady‐state performance evaluation or analysis be conducted in three‐phase domain, or to consider each phase separately
It is unlike transmission systems, where usually single‐phase power flow studies are conducted while considering the system to be balanced.

## Slide 30: 5. Power Flow Studies
To facilitate distribution system analysis, various models shown in the table are used for the components of the system.
Components | Mathematical Model
Substation | Infinite source as a reference bus, where voltage magnitude can be controlled using regulators and/or taps on the transformers
Feeders and Laterals | Three‐phase series impedance and shunt admittance matrices for each line section. Shunt admittance matrix is included for long underground cable with significant charge currents
Load | Complex power for each bus i
DER | Complex power for each bus i
Components | Mathematical Model
Substation | Infinite source as a reference bus, where voltage magnitude can be controlled using regulators and/or taps on the transformers
Feeders and Laterals | Three‐phase series impedance and shunt admittance matrices for each line section. Shunt admittance matrix is included for long underground cable with significant charge currents
Load | 
DER | 

## Slide 31: 5. Power Flow Studies
5.1 Line Model
The above figure shows the schematic of a three- phase line connected between buses i and j.
For simplicity, only the series impedance of the line () is shown.
and is the vector of phase a, b, and c voltages at bus i and bus j respectively,
is the vector of currents flowing in phases a, b, and c voltages from bus i to j of the line.
Fig: Schematic of a three-phase line connected between buses i and j

## Slide 32: 5. Power Flow Studies
5.1 Line Model
Then, we have the expressions as,
is a 3 X 3 matrix, which is realized after reducing a fourth-order model of the line by Kron’s reduction.
For a two‐phase line, matrix has nonzero entries in the 2 × 2 submatrix corresponding to the phases of the line.
For a single‐phase line, it has nonzero entry in the diagonal entry corresponding to the phase of the line.

## Slide 33: 5. Power Flow Studies
5.2 Load and DER Model
Y-Connected:
For modeling loads and DER (negative load), we consider that the real and reactive power for each of the three phases are known separately.
For a three‐phase Y‐connected load, the complex power drawn is shown in the Figure. For this load connected at bus i, as shown in the figure, the vector of complex power is given by:
Fig: Representation of a three-phase Y-connected Load on bus i

## Slide 34: 5. Power Flow Studies
The vectors of voltages and currents at bus i are given by,
, and
Now, consider a matrix operation , which gives the following matrix:
Hence,

## Slide 35: 5. Power Flow Studies
And,
Note that for two‐ or single‐phase loads, , , and must be truncated by removing the entries for phases that do not exist in the load.

## Slide 36: 5. Power Flow Studies
Delta- Connected:
Consider a -connected load as shown in the figure.
A relationship between complex powers, voltages, and currents is,
Fig: Representation of a three‐phase Δ‐connected load on bus i.

## Slide 37: 5. Power Flow Studies
And,
Following that, we can compute using Kirchhoff's current law (KCL),

## Slide 38: 5. Power Flow Studies
5.3 Computing Currents
Knowing the load or demand vectors at each bus, the corresponding current vectors can be found using following equation given the voltage vectors at the buses.

## Slide 39: 5. Power Flow Studies
5.3 Computing Currents
The above figure shows two three‐phase feeders connected between buses i, j, and k with respective loads at these buses.
Fig: Schematic showing line sections and connected loads.

## Slide 40: 5. Power Flow Studies
, , and are load current vectors at buses i, j, and k, respectively.
and are current vectors of currents flowing on lines between buses i and j, and j and k.
is vector of currents entering bus i from bus h, and is vector of currents leaving bus k toward bus l.

## Slide 41: 5. Power Flow Studies
Applying KCL at buses, i, j, and k, we get,

## Slide 42: 5. Power Flow Studies
Similar equations can be written for additional sections in the system. If there are additional feeders splitting off of the main feeder, the KCL can be expanded. For example, consider a case where two feeders are splitting at bus k as shown in the Figure:
Applying the KCL at bus k gives:
Again, if some of the feeders are two or single phase, the equations are modified to include only the phases that exist for a given line section.
Fig: Feeders splitting at bus k.

## Slide 43: 5. Power Flow Studies
5.4 Power Flow Algorithm
The Source-Load-Iteration (SLI) method is an efficient method for radial distribution system power flow analysis.
Computation is done in per-unit (pu) for ease of analysis.
Conversion of the impedances and loads to pu values are required using appropriate base values.
Fig: Feeders splitting at bus k.

## Slide 44: 5. Power Flow Studies
Step 1:
The voltage at the substation is fixed or regulated; therefore, it is known. With substation declared as bus 1 of the system, we get

## Slide 45: 5. Power Flow Studies
Step 2:
Assume a flat profile for all the other bus voltages and set initial values of voltage vectors at all the buses equal to the substation bus, that is
Note: (o) in the superscript is the iteration count, and is the total number of buses in the system.

## Slide 46: 5. Power Flow Studies
Step 3:
Find the current vectors for all the buses that have loads connected to them using:
Note: m in the superscript is the iteration count, and it should not be confused with bus number m used in the previous section. For DERs, determine and corresponding to the voltage at bus i and the selected control mode while considering the reactive power capability.

## Slide 47: 5. Power Flow Studies
Step 4:
Find for each feeder section j-k (section between bus j and bus k) starting from the bus at the edge of the system and sequentially moving toward the source.
If the system has multiple branches emanating from the main feeder, this must be done for all branches starting from the bus at the edge.

## Slide 48: 5. Power Flow Studies
Step 5:
Determine the voltage drop in each feeder section by proceeding from source to load using:
To determine , we start from bus 1 (or source) with known voltages and move toward the loads to compute the bus voltages sequentially starting with bus 2 ,
For all other buses,

## Slide 49: 5. Power Flow Studies
Step 6:
Check for the tolerance level, which is the difference between voltages in two successive iterations for every bus and for all three phases at each bus.
If all the elements of are less than ε, which is an arbitrarily selected small number for tolerance, for all the buses, the power flow converges.
Typically, a value of 0.001 for ε gives good results. If convergence is not achieved, repeat steps 3–6.

## Slide 50: 6. Voltage Regulation
Maintaining proper voltage in the distribution system is very important. There are numerous methods to improve and control the voltage of primary distribution systems:
Use of load tap changing (LTC) transformers.
Application of voltage regulators in the distribution substation as well as on the feeders.
Application of shunt (or series) capacitors on the feeders or at the distribution substation.
Balancing of loads on primary feeders.
Increasing feeder conductor size.

## Slide 51: 6. Voltage Regulation
Increasing primary voltage level.
Changing feeder sections from single phase to three phase.
Transferring of loads from existing feeders to new feeders.
Installation of new substations and primary feeders.
While several of these options are usually considered during the planning stages, LTCs, regulators, and capacitors provide the best means of achieving good voltage regulation during the operational stages on a continuous basis.

## Slide 52: 6. Voltage Regulation
6.1 Voltage Regulation Definition:
Voltage regulation is the voltage difference between the two ends of a line defined as percentage of the receiving end or downstream voltage.
Mathematically:
where is the magnitude of the sending‐end voltage, and is the magnitude of the receiving‐end voltage.

## Slide 53: 6. Voltage Regulation
Fig: Phasor Diagram
Fig: A feeder of resistance R and reactance X.
6.2 Approximate Method for Voltage Regulation:
From the figure of a feeder on the right,
And the voltage drop on the feeder is,
A phasor diagram for this equation with the condition that current lags voltage by an angle is shown in the figure.

## Slide 54: 6. Voltage Regulation
6.2 Approximate Method for Voltage Regulation:
With as the reference voltage or , and , we get:
Typically, in distribution systems, R is approximately equal to X, and δ is very small. Hence, we can consider cosδ ≈ 1 and sinδ ≈ 0, which makes the imaginary go to zero, and the real part giving voltage drop per mile becomes:

## Slide 55: 6. Voltage Regulation
And, the equation of voltage regulation becomes,
Now, if we consider a load connected at the receiving end, we can compute the corresponding current
And,

## Slide 56: 6. Voltage Regulation
which gives
In practice, the approximate voltage drop is an acceptable measure since the error between the exact and approximate values is negligible.

## Slide 57: 6. Voltage Regulation
In distribution systems, usually Vs, the voltage at the substation, is controlled and held constant for varying loading conditions, which implies that the voltage drop and hence Vr at other buses changes.
Obtaining Vr at a given bus for the given impedance and load values requires iterative solution using power flow method.

## Slide 58: 6. Voltage Regulation
Example:
Consider a 12.47‐kV feeder with three point loads as shown in Figure 4.13. The loads are
S2 = 2.5 MVA with 0.92 lagging power factor,
S3 = 3.0 MVA with 0.90 lagging power factor, and
S4 = 2.0 MVA with 0.95 lagging power factor.
The given impedance of the feeder, z, is (0.258 + j 0.6644) Ω/mi or 0.7127∠68.78° Ω/mi. Find the percent voltage drop at bus 4 of the primary feeder for the stipulated load conditions using the approximate method.
Fig: A single‐phase feeder supplying three point loads.

## Slide 59: 6. Voltage Regulation
Solution:
First, compute impedances, Z, of the line sections by multiplying z by l, which is the length of the feeder sections, or:
Z₁₂ = z · l₁₂ = (0.7127∠68.78° Ω/mi)(1.5 mi) = 1.0691∠68.78° Ω
= 0.3870 + j0.9966 Ω
Z₂₃ = z · l₂₃ = (0.7127∠68.78° Ω/mi)(1 mi) = 0.7127∠68.78° Ω
= 0.258 + j0.6644 Ω
Z₃₄ = z · l₃₄ = (0.7127∠68.78° Ω/mi)(1 mi) = 0.7127∠68.78° Ω
= 0.258 + j0.6644 Ω
Next, compute the line‐to‐neutral voltage at bus 1 for the given line‐to‐line voltage for the feeder, or:

## Slide 60: 6. Voltage Regulation
Assume this voltage to be the reference voltage, or V1 = 7200 ∠ 0°. We also assume that the voltage at each bus remains at 7200 ∠ 0°, and we compute the load currents for each bus, or:
I₄ = (S₄ / V₄)* = (2.0×10⁶ / 7200) ∠ −cos⁻¹(0.95) A
= 92.60 ∠ −18.19° A
I₃ = (S₃ / V₃)* = (3.0×10⁶ / 7200) ∠ −cos⁻¹(0.92) A
= 138.89 ∠ −25.84° A
I₂ = (S₂ / V₂)* = (2.5×10⁶ / 7200) ∠ −cos⁻¹(0.92) A
= 115.74 ∠ −23.07° A
Now, compute the currents in the feeder sections using KCL:
I₃₄ = I₄ = 92.60 ∠ −18.19° A
I₂₃ = I₃₄ + I₃ = 92.60 ∠ −18.19° A + 138.89 ∠ −25.84° A
= 230.9950 ∠ −22.78° A
I₁₂ = I₂₃ + I₂ = 230.9950 ∠ −22.78° A + 115.74 ∠ −23.07° A
= 346.73 ∠ −22.78° A

## Slide 61: 6. Voltage Regulation
Compute voltage drops in each feeder section:
VD₁₂ = I₁₂ [ R₁₂ cos(22.88°) + X₁₂ sin(22.88°) ]
= 346.7340 [ 0.3870 × 0.9213 + 0.6644 × 0.3888 ]= 257.97 V
VD₂₃ = I₂₃ [ R₂₃ cos(22.78°) + X₂₃ sin(22.78°) ]
= 230.9950 [ 0.2580 × 0.9219 + 0.6644 × 0.3872 ]= 114.37 V
VD₃₄ = I₃₄ [ R₃₄ cos(18.90°) + X₃₄ sin(18.19°) ]
= 92.60 [ 0.2580 × 0.95 + 0.6644 × 0.3122 ]= 41.90 V
Thus, the total voltage drop in the entire feeder is the sum of the voltage drops in individual sections, or:
VD₁₄ = VD₃₄ + VD₂₃ + VD₁₂
= 41.90 + 114.37 + 257.97= 414.24 V
Vᵣ = 7200 − 414.24 = 6815.76 V

## Slide 62: 6. Voltage Regulation
Therefore, the percent voltage regulation is
Verify the accuracy on this result by finding the exact solution for this problem by determining voltages with power flow using the source‐to‐load iterative method. You will find that the error is minimal in this case due to the power factors of all three loads being close to each other.

## Slide 63: 6. Voltage Regulation
6.3 Voltage Drop on Radial Feeders with Uniformly Distributed Load
In the previous section, we considered spot loads connected at the buses.
In this section, we consider a case where the loads are distributed uniformly across the length of the feeder in a rectangular service area.
Also, we generalize it for a three‐phase feeder, assuming that all the three phases have identical values of resistance and reactance.

## Slide 64: 6. Voltage Regulation
6.3 Voltage Drop on Radial Feeders with Uniformly Distributed Load
Consider the current density to be k A/mile for the feeder shown in the Figure. With l as the length of the feeder, the current at the sending end is = kl, and the current at the receiving end is 0.
Fig: Feeder with load distributed uniformly in a rectangular service area

## Slide 65: 6. Voltage Regulation
Fig (b) shows the plot of the magnitude of a current assuming that the current throughout the feeder has the same phase angle.
From this figure, we get
or,
Consider a differential element of the feeder of length at a distance . With ohms/mile as impedance of the feeder, the differential voltage across is,
Fig (b): Current on the feeder

## Slide 66: 6. Voltage Regulation
Therefore, the voltage drop on the feeder is
We can also compute losses on the feeder by considering differential power loss with ohms/mile as the resistance of the feeder.
Then, the power loss per phase is

## Slide 67: 6. Voltage Regulation
The total power loss for the three phases is
The results shown above are useful for planning studies because while planning we do not have the system topology and actual load values available. All we have are projected values.
These approximations are also useful in optimizing operating scenarios where precise calculations may slow down the process of obtaining the final solution. In those cases, approximation can be used to narrow the solution space, and precise calculations can be implemented on a smaller solution space, thus, speeding the overall computation in search for the optimal solution.

## Slide 68: 6. Voltage Regulation
6.4 Voltage Drop on Radial Feeders Serving a Triangular Area
This section, we consider a case in which the service area of a feeder is triangular with load distributed uniformly in the service area.
Let be the current density in amperes per square mile.
Next, we get an expression for current at distance .
Substituting the value of gives
Fig: Feeder serving a triangular area with fixed load density

## Slide 69: 6. Voltage Regulation
Note that . Substituting this ,
Again, consider a differential element and write an expression for the differential voltage drop
Further, the voltage drop across the feeder is
or

## Slide 70: 6. Voltage Regulation
Similarly, we can find power loss, which is
Then, the power loss per phase is
And,

## Slide 71: 7. Fault Calculation
The standard procedure for fault calculation in power systems requires determining Thevenin's equivalent for positive‐, negative‐, and zero‐sequence networks at the point of fault.
The sequence networks are connected to each other based on the type of fault.
However, decoupling of circuits in the sequence domain works only under the conditions of symmetry.

## Slide 72: 7. Fault Calculation
For example, consider a three‐phase feeder with impedance matrix in the phase domain as shown below,
The conditions of symmetry require that,
, and

## Slide 73: 7. Fault Calculation
While for transmission lines these are satisfied with transposition, they are not feasible for distribution feeders. Distribution feeders are rarely transposed and also can be of two or one phase in addition to three phases.
Since single‐ and two‐phase feeders do not have models in the sequence domain, symmetrical component‐based analysis is not applicable to them. Also, for three‐phase part of the system, symmetrical components do not provide any advantage because the sequence impedance matrix is not diagonal.

## Slide 74: 7. Fault Calculation
Hence, positive‐, negative‐, and zero‐sequence impedances cannot be decoupled from one another.
However, we can implement a solution technique in phase domain to determine fault currents in distribution systems. We initially consider a radial distribution system connected to the bulk power system with no additional sources in the system.

## Slide 75: 7.1 Prefault System
A general distribution feeder connected to the substation bus with multiple feeder sections as shown in the Figure. While the main feeder is a three‐phase feeder, the laterals can be three, two, or single phase. Each feeder section is modeled by its impedance matrix.
For illustration, we are considering delta‐wye‐grounded connection for the transformer, but the method will work for other configurations too.

## Slide 76: 7.1 Prefault System
The system in the figure represented in the oval represents the entire power system upstream of the transformer.
This system can be represented by a Thevenin equivalent impedance matrix and a voltage source vector for the three phases.
Fig: An example Distribution System

## Slide 77: 7.1 Prefault System
The equivalent voltage source is considered balanced with 1 pu magnitude, i.e.
where subscript s is the source.
All the prefault load currents are considered to be 0 with the assumption that load currents are much smaller compared to the fault current.

## Slide 78: 7.1 Prefault System
Directly determining the Thevenin equivalent matrix in the phase domain is difficult. An indirect approach is considered due to the difficulty.
Utilities usually have information on equivalent positive‐, negative‐, and zero‐sequence impedance values at different buses in the transmission system.
The values can also be computed using the approach discussed in Section 2 of the slide (Modeling of Source Impedance).
The values are denoted as , , and at bus m.
The zero‐sequence impedance value only includes the impedance of the transformer due to the selected transformer connection.

## Slide 79: 7.1 Prefault System
Delta/wye‐grounded transformers create an open circuit in the zero‐sequence circuit, where current flows through the transformer only on the wye‐grounded side.
The transmission system is assumed to be fully balanced. As a result, the sequence networks are decoupled.

## Slide 80: 7.1 Prefault System
The impedance matrix of the system in the sequence domain can be written as follows:
Now, we use transformation to convert this matrix to phase domain

## Slide 81: 7.1 Prefault System
where a is a complex number equal to 1∠120o
Let bus i be the candidate bus for faults.
Since all the feeder sections between the substation bus (bus m) and the faulted bus are in series, we can add their impedance matrices to compute the equivalent impedance matrix.
All the feeder sections not in the path from the substation to the faulted bus do not influence the fault current and thus are not included in the calculations.
Consider this matrix to be:

## Slide 82: 7.1 Prefault System
Now, this matrix is added to the system impedance matrix to get the impedance matrix from the equivalent source to the faulted bus,
Note: This summation can only be done if both matrices on the right‐hand side are in per unit, or impedances are referred to the low‐voltage side of the transformer due to different voltage levels of the distribution system and the bulk power system.

## Slide 83: 7.2 Three – Phase Fault
For a three‐phase fault at bus i, current will flow from the substation to bus i.
Since there is no additional source, no other currents will flow.
Also, we assume that the fault impedance is 0.
Fig: Three – phase fault at bus i

## Slide 84: 7.2 Three – Phase Fault
If the fault is a high impedance fault, these assumptions will not be fully valid. The Figure above shows the conditions for a three‐phase fault.
The fault currents are, .

## Slide 85: 7.2 Three – Phase Fault
The equation from the voltage drop from the source to bus i is,
For a solidly grounded fault, all the voltages at bus i will be 0.

## Slide 86: 7.2 Three – Phase Fault
Applying this condition and substituting values of the source bus voltage, we get,
In the next step, we get,

## Slide 87: 7.2 Three – Phase Fault
If the system has additional sources, they can be applied one at a time while removing the equivalent source at the substation.
Source impedance matrix needs to be known and the equivalent impedance matrix from each source to bus i must be determined.
Voltages at the source terminal are required for the calculations.

## Slide 88: 7.2 Three – Phase Fault
For inverter-based sources, their characteristics under faults and operating rules must be known.
Some inverter‐based sources are automatically disconnected during fault, and most are adjusted to produce a smaller current by adjusting the impedance of inverter, which makes fault calculations challenging.
However, if we can compute fault currents for all the sources one at a time, all the fault currents can be added using superposition to compute the cumulative current.
Since the circuit is linear, superposition can be applied without affecting the results.

## Slide 89: 7.3 Double-Line-to-Ground (DLG) Fault
For a fault at bus i, current will flow from the substation to bus i on the two faulted phases and no current on the third phase. As shown in the Figure, a fault between phases b and c is considered.
The currents for this fault are
The voltage drop equation from the source to bus is:
Fig: DLG fault between phases b and c at bus i.

## Slide 90: 7.3 Double-Line-to-Ground (DLG) Fault
Discard the first row and the first column and write the equations in a reduced form, as,
Further,
The same approach can be used for faults on any other two phases.

## Slide 91: 7.4 Single-Line-to-Ground (SLG) Fault
For a fault at bus i, current will flow from the substation to bus i on the faulted phase and no current on the other two phases.
For illustration, we consider a fault on phase a as shown in the figure.
The currents for this fault are
We can write an equation for voltage drop from the equivalent source to bus as,

## Slide 92: 7.4 Single-Line-to-Ground (SLG) Fault
Discard the last two equations and keep only the first one, or
Therefore,
Again, the same approach can be used for faults on other phases.

## Slide 93: 7.5 Line-to-Line (LL) Fault
For an LL fault at bus i, current will flow from the substation to bus i on the faulted phases and no current on the third phases.
For illustration, we consider a fault between phase b and c as shown in the figure.
For this fault, the currents will not flow to the ground but return through the second phase, as,
Hence, the currents for this fault are:
Fig: DLG fault between phases b and c at bus i.

## Slide 94: 7.5 Line-to-Line (LL) Fault
Also, the voltages at bus for the faulted phases are equal,
Therefore, the equation for voltage drop from the equivalent source to bus is
Expanding the last two equations gives
And.

## Slide 95: 7.5 Line-to-Line (LL) Fault
Rearranging and expressing in the matrix form gives
Solving it gives both and as well as and .

## Slide 96: 7.6 Symmetrical Component-based Fault Analysis
Although symmetrical component‐based fault analysis does not work well for distribution systems, it can be used to get approximate results only for the part of the system that has all the three phases.
The first step is to determine the three-phase impedance matrix from the substation bus (bus m) to the faulted bus (bus i).
The general equation for this impedance matrix is given by,

## Slide 97: 7.6 Symmetrical Component-based Fault Analysis
The next step is to transform this matrix to sequence domain, which gives:

## Slide 98: 7.6 Symmetrical Component-based Fault Analysis
The resulting sequence impedance matrix is not diagonal, but for approximation, we discard the off-diagonal terms.
The diagonal entries are considered as the zero-, positive, and negative-sequence impedances of the distribution system from the substation bus to the point of fault.
To determine the pre-fault circuits in the sequence domain, we add the respective impedances from the equivalent source to the substation bus and the impedances from the substation bus to the faulted bus.

## Slide 99: 7.6 Symmetrical Component-based Fault Analysis
All impedances must be converted to per unit before adding them.
The voltage source in the phase domain is balanced, providing a source only for the positive sequence.
Hence, we can determine the three pre-fault sequence domain circuits as shown in the figure (next slide).

## Slide 100: 7.6 Symmetrical Component-based Fault Analysis
Fig: Pre-fault positive‐, negative‐, and zero‐sequence equivalent circuits with respect to bus i.
Note that in the figure,

## Slide 101: 7.6.1 Three-phase Fault
For a three‐phase fault, the system stays balanced, and the negative‐ and the zero‐sequence currents are 0.
To compute the positive‐sequence current, we create a short circuit across the positive‐sequence circuit as shown in Figure.
Fig: Three‐phase fault in sequence domain.

## Slide 102: 7.6.1 Three-phase Fault
From this circuit,
Now, we convert them to the phase domain,

## Slide 103: 7.6.2 DLG Fault
The conditions for this fault in phase domain are
and .
Transforming these conditions to sequence domain gives,
And,
Simplifying gives,
or,
Fig: DLG fault in sequence domain.

## Slide 104: 7.6.2 DLG Fault
Also,
or,
Therefore,
We use conditions given by:
and , to create the circuit in sequence domain shown in the Figure .

## Slide 105: 7.6.2 DLG Fault
and,
The sequence currents and voltages can be transformed to the phase domain using the relevant equations.

## Slide 106: 7.6.3 SLG Fault
The conditions for this fault in phase domain are and .
Transforming these conditions to sequence domain gives
or,
Also,
Based on the above two equations, we can create a circuit shown in the Figure.
Fig: SLG fault in sequence domain.

## Slide 107: 7.6.3 SLG Fault
From this circuit, we get
And,
Fig: SLG fault in sequence domain.

## Slide 108: 7.6.4 LL Fault
The conditions for this fault in the phase domain are , and .
Transforming these conditions to sequence domain gives
and
Therefore,
and

## Slide 109: 7.6.4 LL Fault
or
Based on the equations,
, and , we can create a circuit as shown in the figure.
and
Fig: LL fault in sequence domain.

## Slide 110: Thank You!