## Slide 1: Distribution System Operation and Automation
Dr. Zhaoyu Wang
1113 Coover Hall, Ames, IA
wzy@iastate.edu
ECpE Department

## Slide 2: Distribution System Operation and Automation
ECpE Department
Acknowledgement:
The slides are developed based in part on Electric Power and Energy Distribution Systems, Models, Methods and Applications, Subrahmanyan S. Venkata, Anil Pahwa, IEEE Press & Wiley, 2022

## Slide 3: 1. Overview
Distribution system operation involves various switching activities:
  Restoration after outages
  Substation maintenance and clearance
  Load transfers to alleviate overloads
  Capacitor switching
  System reconfiguration
  Disabling automatic reclosing for live line work and turning on instantaneous tripping for live line work
  Temporary switching for other work and planned outages
Usually, all planned switching operations should be done without any interruption of service.
ECpE Department

## Slide 4: 1. Overview
A midsize US utility typically executes 10 to 20 switching orders per day in a distribution system, varying in length from a few steps to hundreds. Most are planned operations with written instructions to respond to a switching request, while some relate to outages. The number can be weather-dependent, surging into the hundreds during severe weather conditions.
Around 4500 switching orders were reported by a utility in 2008. The number has escalated due to increased maintenance spending, and more outages due to severe weather and an aging system.
ECpE Department

## Slide 5: 1. Overview
Monitoring substation alarms from SCADA, processing outage management, and troubleshooting, the distribution control center is responsible to determine whether switching requests can be granted after proper system analysis.
Conventionally, most of the distribution system operations are executed manually. With the advancements in communications and computer technology, they are gradually becoming automated, which brings the concept of distribution automation (DA).
ECpE Department

## Slide 6: 2. Distribution Automation
Deregulation and restructuring push utilities towards higher supply reliability and quality at distribution level. Meanwhile, utilities aim to improve system efficiency by reducing system losses.
Originating in the 1970s, DA evolved with monitoring, control, and communication technologies. It provides real-time computation, communication, and control of distribution systems.
Progress of DA has been relatively slower in distribution systems than in generation and transmission systems. The main reason is the utilities’ cost concern.
ECpE Department

## Slide 7: 2. Distribution Automation
However, DA provides many intangible benefits:
  It provides flexible control of distribution systems, which enhances efficiency, reliability, and quality of electric service.
  It leads to more effective utilization and life extension of the existing distribution system infrastructure and enhances system resiliency.
ECpE Department

## Slide 8: 2. Distribution Automation
DA functions can be categorized into monitoring and control functions.
  Monitoring functions include recording meter readings, switching device status, and abnormal events.
  Control functions involve switching operations, system protection, and some specific customer service (e.g. automated meter reading, remote load control and demand response).
Application of distribution‐level power electronic devices can benefit the control in a rapid time frame: STATCON, inverter‐based resources.
Evolving as part of AMI, a separate area of smart grid.
ECpE Department

## Slide 9: 2. Distribution Automation
Those devices with DA are supposed to integrate to deliver high quality electric power to the end users, but the implementation in distribution systems is limited.
Equipment reliability was a major concern until the early 1990s.
Equipment available now is more reliable and robust, but still several issues remain, like cost, hardware and software standards, and interoperability.
ECpE Department

## Slide 10: 2. Distribution Automation
DA implementation requires careful planning. Two approaches can be adopted: top-down and bottom-up.
  Top-down: revolutionary, large‐scale, fully integrated automation system with all or most functions.
  Bottom-up: evolutionary, integrate automation devices for only selected functions, or a small part of system. Other functions or parts can be automated gradually.
The top‐down approach is expensive and requires great modifications, so it is suitable for only a few utilities.
ECpE Department

## Slide 11: 2. Distribution Automation
The bottom‐up strategy is more suitable for a majority of utilities since it allows them to adjust gradually and install automated systems for their immediate needs.
The main difficulty for contemplating DA is to identify the functions to be automated. It can depend on geographic location, operating philosophy, and financial situation.
ECpE Department

## Slide 12: 3. Communication Infrastructure
DA system relies on communication infrastructure to connect customer locations, control points, and energy management system.
Communication infrastructure is hybrid, utilizing various mediums for different parts.
Early DA systems used telephone for communication between the control center and the substation and PLC/radio between substation and customers.
PLC-based communications suffered from attenuation (specifically transformers), and gradually decreased in popularity.
ECpE Department

## Slide 13: 3. Communication Infrastructure
Advances in radio technology and the availability of the 900 MHz frequency spectrum make radio a popular and reliable communication medium.
Fiber optic cables are used along feeders to concentrators, then radios can reach customers from those points.
Cellular telephone technology can also be used for some applications in distribution systems.
Satellite communication has been experimented with, but not widely used.
ECpE Department

## Slide 14: 4. Distribution Automation Functions
DA functions can be categorized into customer-level and system-level functions.
  Customer-level functions: require communication-capable devices at customers’ premises, including meter reading, demand response, time-of-use rates, outage alerts, and remote connect/disconnect.
  System-level functions: related to system operations, devices installed at substations and feeders, including fault detection and service restoration, feeder reconfiguration, voltage/VAR control, equipment monitoring, and digital protection.
This chapter focuses on system operation-related functions, while customer-related functions can be implemented as a part of AMI.
ECpE Department

## Slide 15: 4. Distribution Automation Functions
Operation-related functions can be divided into substation- and feeder-related functions.
Four important functions are covered: (1)outage management, (2)feeder reconfiguration, (3)voltage and reactive power management, and (4)equipment monitoring and control. Substation and feeder functions can overlap and be coordinated in some cases.
ECpE Department

## Slide 16: 4.1 Outage Management
Distribution systems, particularly with a large percentage of overhead feeders, are susceptible to various types of faults due to exposure to the environment. While underground feeders are not exposed to several environmental factors, they also experience faults.
Also, a large majority of distribution systems around the world are overhead due to cost considerations. Since underground feeders typically cost 5–10 times more than overhead feeders, so they are used only in special situations where aesthetics or higher reliability is of concern.
ECpE Department

## Slide 17: 4.1 Outage Management
The system can have either a temporary or a permanent fault.
  For a temporary fault, the affected customers experience interruption of power for a very short duration, which is typically in seconds.
  In the event of a permanent fault, the protective devices are expected to operate and isolate the faulted section, which results in longer service interruption for the customers.
However, if the fault is of a high impedance type, the protective devices might not operate to isolate the faulted section. In such situations, locating faults becomes more difficult.
ECpE Department

## Slide 18: 4.1 Outage Management
If no information on the status of various devices in the distribution system is available to the distribution system dispatchers, there is no direct way to find out about the outages. The dispatchers depend on telephone calls from customers or a sudden change in power flow at a metered location upstream in the system to come to know of the outages. Calls from customers only provide an approximate location of the outage.
Moreover, in the case of a major storm, multiple outages can be widespread and difficult to locate:
  Once the approximate location of outages is known, line crews are dispatched to drive along the lines to look for damage.
  After the damaged area is located, it has to be isolated from the rest of the system if the protective devices have not done that already.
ECpE Department

## Slide 19: 4.1 Outage Management
  The next step is to restore power to those parts of the system that are undamaged but have power interruption due to problems elsewhere in the system. The power to these parts may be provided from alternates routes. The dispatchers determine such possible routes and ask the line crew to operate switches. Many of the switches cannot be operated under load; therefore, the substation breaker has to be opened before operating them.
If the whole process is done manually, it takes a long time.
ECpE Department

## Slide 20: 4.1 Outage Management
Automation of this function requires installation of remotely controlled sectionalizers and sensors on the feeders and leveraging AMI at customer locations to detect interruption of service.
Upon loss of power, the meter automatically sends a message, or the outage is detected when the metered information is not received at the end of the metering duration. In the latter case, there can be a delay up to the metering duration, for example 15 minutes, if the outage happens at the beginning of the metering duration.
Since the activity of locating outages has historically depended on customer calls, it is called Trouble Call Analysis in the utility jargon.
ECpE Department

## Slide 21: 4.1 Outage Management
Once sufficient calls are received, locations of the outages are determined based on the escalation of data from the customer level to the substation level.
To aid the operators in an outage location, the calls are automatically mapped on the system map. However, simple escalation can lead to wrong diagnosis, specifically during multiple outages. Therefore, advanced inferencing techniques are used to determine possible locations of faults. Installation of sensors on the feeders to obtain additional information also increases the possibility of correct diagnosis. One approach requires recording the time of service interruption at different locations in the system. Techniques based on voltage sags are also used for location of outages. In general, it is easier to locate the main feeder outages but more difficult to locate lateral outages.
ECpE Department

## Slide 22: 4.1 Outage Management
The next step is the restoration of service to customers.
  If the fault happens on the main feeder, power to the unfaulted section of the feeder is restored by automatically closing a tie switch, which routes power from a neighboring feeder. Following that, the crew is directed toward the faulted section to fix the problems, and to restore service.
  If the fault is on a lateral, restoration requires replacing the fuse manually after the crew has made repairs. Laterals usually do not have a tie switch from a neighboring lateral.
ECpE Department

## Slide 23: 4.1 Outage Management
Also, replacing fuse by an automated sectionalizer is a very expensive proposition because a distribution system of a small city may have hundreds of laterals. With the cost of an automated single‐phase sectionalizer about $10,000 and the cost of a fuse for the same lateral about $50, it is difficult to justify replacing the fuse by an automated sectionalizer.
As automation of this function provides more precise location of the outages, the crew goes to the identified location instead of looking for problems in a general area. Thus, with automation, the whole process of outage location and service restoration can be accomplished more efficiently by less people in much less time with minimum interruption to the customers.
ECpE Department

## Slide 24: 4.2 Feeder Reconfiguration
Load variation occurs hourly, daily, and seasonally in distribution systems.
Optimal feeder configuration is crucial. Previously focused on minimum losses. Service reliability now is equally important.
Multi-objective reconfiguration includes objectives like loss minimization, load balancing, and voltage deviation.
Reconfiguration involves opening closed switches and closing open ones while maintaining radial structure and continuous power supply.
ECpE Department

## Slide 25: 4.2 Feeder Reconfiguration
Manual reconfiguration is seasonal and infrequent due to complexity and service interruptions.
Automated reconfiguration uses sectionalizers for fault isolation and restoration. Remote control allows more frequent reconfiguration.
Challenges include:
  Creating loops temporarily, then restoring radial structure.
  Switch wear and tear, impacts switch lifespan.
  Trade-off between benefits of frequent reconfiguration and switch replacement cost.
ECpE Department

## Slide 26: 4.3 Voltage and VAr Management
Voltage and reactive power management is crucial for ensuring proper service voltage and minimizing losses.
Customer loads are mainly inductive, necessitating capacitors for reactive power compensation.
Coordination between LTC at the substation transformer, switched capacitors, and line regulators is essential.
Substation LTC ensures proper voltage levels from the transformer.
ECpE Department

## Slide 27: 4.3 Voltage and VAr Management
Switched capacitors provide reactive power compensation in the distribution system.
Line regulators help maintain voltage levels by adjusting tap positions.
Proper management of these devices ensures efficient system performance and customer satisfaction.
ECpE Department

## Slide 28: 4.3.1 Transformer LTC Operation
LTC (Load Tap Changer) adjusts tap position in response to load. Higher load causes more voltage drop on feeders. Tap moves higher to maintain proper voltage along feeders. Lower load results in lower voltage drop; tap moves lower.
LTC responds to feeder voltage measured at substation to maintain voltage levels across the system.
Another approach is the line-drop compensation scheme regulates voltage at specific points on feeders using voltage-regulating relays.
Relay voltage = Substation voltage - Estimated feeder voltage drop.
ECpE Department

## Slide 29: 4.3.1 Transformer LTC Operation
Previously, there’s no direct voltage measurements on feeders. Control was based on estimations and effected by the customers at the end of the feeder.
Now, utilities are installing voltage measurements, typically at the end of the feeder to provide precise and optimal control of LTC. It also enables implementation of conservation voltage reduction (CVR) strategies to reduce system demand.
ECpE Department

## Slide 30: 4.3.2 Capacitor Operation
Capacitors in distribution systems provide voltage and reactive power support. Capacitors can be fixed or switched, strategically placed for system improvement. The switch status is based on signal from controlling device:
  Timer-based control assumes load patterns but doesn't account for variations or holidays. Temperature-sensitive control has limitations due to lag in air-conditioning demand.
  Microprocessor-based controllers with communication offer improved control. It communicates with central station for coordination, but don't consider system-wide impacts.
ECpE Department

## Slide 31: 4.3.2 Capacitor Operation
Optimal Capacitor Configuration:
  Achieved with higher automation level.
  Meters are required to measure real/reactive power, voltage, current.
  Data sent to central computer for optimal switching.
  Minimize losses, keep voltages within limits.
ECpE Department

## Slide 32: 4.3.2 Capacitor Operation
Benefits of real-time measurement capabilities :
  Allows frequent switching for optimal operation.
  Prevents frequent switching to avoid equipment failure.
  Addresses power quality concerns.
Future Prospects:
  Power electronics-based schemes for reactive power control.
  Eliminate concerns of mechanical switching.
ECpE Department

## Slide 33: 4.3.3 Regulator Operation
Voltage regulators are autotransformers used in distribution systems for voltage control.
They are especially useful on long distribution lines with high voltage drops.
Regulators are set to maintain voltage within a specified range.
When voltage drops below the low setting, the tap moves to increase output turns.
When voltage exceeds the high setting, the tap moves to reduce output turns.
ECpE Department

## Slide 34: 4.3.3 Regulator Operation
Regulators use line drop compensation to regulate voltage at a specified downstream point.
Implementation of DA allows actual voltage measurements for regulator control.
DA enables coordination of regulator operation with capacitor switching for loss reduction and improved voltage profile.
Better voltage profile leads to fewer low voltage complaints from customers.
ECpE Department

## Slide 35: 4.3.4 Smart Inverters
Impact of Increased IBR (Inverter-Based Resources) Proliferation:
  Integration of IBRs like solar PV challenges voltage and var management.
  Injection of real power causes voltage rise.
  Intermittent solar PV output leads to voltage fluctuations.
Smart Inverter Evolution:
  Earlier inverters lacked reactive power control options.
  Currently, inverters can offer smart reactive power control.
  Options for local or coordinated control.
ECpE Department

## Slide 36: 4.3.4 Smart Inverters
Challenges of Coordinated Control:
  Coordinated control requires fast data processing and communication.
  Centralized control in large systems is impractical.
  Hybrid approach with distributed data management is feasible.
Data Ownership and Control:
  Customer-owned rooftop solar PV behind the meter.
  Utilities lack data access and control jurisdiction.
  Control necessitates special agreements between utilities and customers.
ECpE Department

## Slide 37: 4.3.4 Smart Inverters
FERC Order 2222 and Aggregators:
  FERC order allows third-party aggregators to coordinate behind-the-meter resources.
  Aggregators gain data access and control over devices.
  Need for coordination between aggregators and utilities.
Complexities of Aggregator Coordination:
  Many aggregators involved with customers in a distribution system.
  Balance needed to prevent adverse impacts on distribution systems.
ECpE Department

## Slide 38: 4.3.4 Smart Inverters
Potential Smart Inverter Architecture:
  The figure illustrates an architecture for leveraging smart inverters.
  Investigation ongoing, no single solution yet.
Fig. An architecture for transactive energy in distribution systems
ECpE Department

## Slide 39: 4.4 Monitoring and Control
Distribution system monitoring serves a purpose similar to traditional SCADA systems.
Monitoring is essential for data acquisition for various distribution functions.
Real-time data is required for functions that make immediate control decisions.
Real-time data provides alarms to operators for abnormal system conditions.
ECpE Department

## Slide 40: 4.4 Monitoring and Control
System data can be archived for future use in forecasting and planning.
Monitoring assists in managing major assets like substation transformers and circuit breakers.
Monitoring plays a crucial role in various aspects of distribution systems.
ECpE Department

## Slide 41: 4.4.1 Transformer Life Extension
Substation transformer are usually operated below capacity, but can handle emergency overloads. Overloading should be limited by time to avoid damaging transformers.
In manual processes, dispatchers use trial and error for load management. They close switches to add load, aiming for a certain limit. If actual load surpasses this, they open switches, disconnect feeders, and repeat the process. Frequent switching strains transformers, shortening their lifespan.
ECpE Department

## Slide 42: 4.4.1 Transformer Life Extension
Proper monitoring: reduces switching operations, minimizes transformer stress
  Monitor the oil and winding temperatures determine the level of overloading.
  Select feeders for balanced loading and desired levels.
  Limit the overloading of the transformers without too many switching operations.
Such monitoring and control of distribution transformers is very challenging due to a large number of such transformers in the system and high expense. But with increased EV and rooftop PV, the monitoring of transformers can be more essential.
ECpE Department

## Slide 43: 4.4.2 Recloser/Circuit Breaker Monitoring and Control
Remote Monitoring and Control Limitations:
  Circuit breakers and reclosers lack remote monitoring and control.
  Settings adjustments require physical presence at equipment location.
  Pole-mounted reclosers' settings changes are time-consuming.
Maintenance Challenges Without Monitoring:
  Contacts of reclosers and circuit breakers refurbished at fixed intervals.
  Maintenance frequency often conservative, leading to premature service.
ECpE Department

## Slide 44: 4.4.2 Recloser/Circuit Breaker Monitoring and Control
Benefits of Automation:
  Automated scenario allows remote relay settings and recloser timings.
  Improved system control and protection during configuration changes.
  Remote settings save labor for adjustments.
  Precise energy interruption monitoring for contact health assessment.
ECpE Department

## Slide 45: 4.5 Cost – Benefit of Distribution Automation
Assessing costs and benefits is crucial for DA implementation decisions. Automation costs include communication, hardware, software, training, etc.
Categories of Benefits:
  Efficiency: reduced losses, peak power demand, and manpower needs.
  Reliability: fewer, shorter power interruptions, equipment failure prevention.
  Power quality: fewer momentary interruptions, voltage issues.
  Resiliency: aiding recovery from extreme weather events.
ECpE Department

## Slide 46: 4.5 Cost – Benefit of Distribution Automation
In essence, the process involves:
  Mapping DA functions to operational benefits.
  Mapping operational benefits to monetary benefits.
  Comparing outcomes with existing methods.
  Estimating values for missing or uncertain variables.
  Conducting sensitivity analysis to determine key variables.
This approach enables utilities to make informed decisions regarding the implementation of DA functions based on their cost-effectiveness and potential benefits.
ECpE Department

## Slide 47: 4.5 Cost – Benefit of Distribution Automation
Table: Mapping the benefits of distribution automation functions.
ECpE Department
DA functions | Higher energy sales | Lower SAIFI | Lower SAIDI | Life extension of equipment | Lower losses | Reduced peak demand | Reduced manpower | Lesser low-voltage complaints
Outage management | X | X | X | X |  |  | X | 
Feeder reconfiguration |  |  | X | X | X |  |  | X
Voltage/var management |  |  |  |  | X | X | X | X
Monitoring and control |  | X | X | X |  |  | X | 

## Slide 48: 4.5 Cost – Benefit of Distribution Automation
To illustrate the computation of monetary benefits of different operation benefits, few examples of operational benefits of outage management are provided below.
4.5.1 Higher Energy Sales
With faster restoration, the customers receive service sooner than with the traditional approach.
This in turn results in additional revenues for the utility for selling electricity to the customers.
ECpE Department

## Slide 49: 4.5 Cost – Benefit of Distribution Automation
4.5.2 Reduced Labor for Fault Location
With automation, faults can be located sooner, which saves time spent on the task for the field crew as well as the operators.
This in turn results in labor cost savings.
ECpE Department

## Slide 50: 4.5 Cost – Benefit of Distribution Automation
4.5.3 O&M of Switches and Controllers
Automated switches will have different failure rates and repair cost than the manual switches. Difference in these costs must be accounted.
This quantity will be a benefit if it is positive and will be additional cost if it turns out to be negative.
ECpE Department

## Slide 51: 4.5 Cost – Benefit of Distribution Automation
4.5.4 Lesser – Low – Voltage Complaints
Automation is expected to provide better voltage at customer ends, which will result in lower low‐voltage complaints.
This will result in savings because the utility has to spend time and resources to investigate the cause of such complaints.
where X is the complaints without automation per thousand customers per year and X' is the complaints with automation per thousand customers per year.
ECpE Department

## Slide 52: 4.6 Cost – Benefit Case Study
Example Systems and Functions:
  Urban and rural distribution systems considered for DA implementation.
  All functions considered for automation in rural system.
  In urban system, all except voltage regulator control.
Data and Analysis Software:
  Data from [1] is used for the systems. A summary is provided in Table1.
  Economic analysis duration: 15 years.
  PC-ADAM software [2] is utilized for analysis.
Table1. Data for the two example systems.
  [1] Willis, H.L. (1997). Power Distribution Planning Reference Book. New York, NY: Marcel Dekker, Inc.
  [2] Shultis, J.K. and Pahwa, A. (1992). A User's Guide for PC‐ADAM. Research Report 237, Kansas State Eng. Expt. Stn. (June 1992).
ECpE Department
Parameter | Urban system | Rural system
Number of substations | 5 | 4
Number of transformers per substation | 3 | 3
Number of feeders per transformer | 3 | 1
Total length of primary feeders | 288 | 292
Customer density (per sq. mile) | 525 | 3.5
Power consumption (kW/customer) | 6.19 | 3.77
Total area served (sq. mile) | 90 | 1000
Total number of customers | 47,250 | 3,500

## Slide 53: 4.6 Cost – Benefit Case Study
Table2. Summary of all costs and benefits for the urban system.
Table3. Summary of all costs and benefits for the rural system.
ECpE Department
No. | Description | Benefits ($) | Costs ($) | B/C ratio
 | Initial planning and equipment cost | — | 339,829 | 
 | Intangible benefits | 197,208 | — | 
1 | Outage management | 1,195,716 | 1,032,612 | 1.16
2 | Option 1 + feeder reconfiguration | 3,236,062 | 1,038,393 | 3.12
3 | Voltage and var management |  |  | 
 | Transformer LTC operation | 18,192 | 19,654 | 0.93
 | Capacitor operation | 996,435 | 200,299 | 4.97
4 | Monitoring and control |  |  | 
 | Distribution system monitoring | 1,680,210 | 500,512 | 3.36
 | Transformer life extension | 114,086 | 70,046 | 1.63
 | Recloser/circuit breaker monitoring and control | 157,199 | 86,709 | 1.81
All selected options | All selected options | 8,079,603 | 2,755,953 | 2.93
No. | Description | Benefits ($) | Costs ($) | B/C ratio
 | Initial planning and equipment cost | — | 174914 | —
 | Intangible benefits | 98604 | — | —
1 | Outage management | 1800333 | 437790 | 4.11
2 | Option 1 + feeder reconfiguration | 1918271 | 443571 | 4.32
3 | Voltage and var management |  |  | 
 | Transformer LTC operation | 16920 | 16186 | 1.05
 | Capacitor operation | 366483 | 152608 | 2.33
4 | Monitoring and control |  |  | 
 | Distribution system monitoring | 821173 | 181436 | 4.53
 | Transformer life extension | 12697 | 57193 | 0.22
 | Recloser/circuit breaker monitoring and control | 54784 | 33528 | 1.63
All selected options | All selected options | 4129591 | 1253588 | 3.29

## Slide 54: 4.6 Cost – Benefit Case Study
Benefit/cost analysis shown in Table2 and Table3. The overall benefit/cost ratio are 2.93 for urban system and 3.29 for rural system, both beneficial.
Outage management: 1.16 (urban), 4.11 (rural), due to the fact that rural systems are spread out, making it harder to locate faults and to restore service.
When feeder reconfiguration is included, the benefit/cost ratio changes to 3.12 for the urban system and 4.32 for the rural system. This implies that addition of this option is beneficial in both cases, but it is significantly more for the urban system with larger load.
ECpE Department

## Slide 55: 4.6 Cost – Benefit Case Study
The benefit/cost ratio for transformer TLC operation in both cases are close to 1, implying the benefits are almost equal to cost. It means existing LTC control works very well.
Voltage and var management with switched capacitors have a benefit/cost ratio of 4.97 for the urban system and 2.4 for the rural. It means loss reduction is significant, especially in urban system.
The benefit/cost ratio for distribution system monitoring is 3.36 for the urban system and 4.53 for the rural system. Slight extra benefit in rural systems is due to the reduced data collection cost.
ECpE Department

## Slide 56: 4.6 Cost – Benefit Case Study
Transformer life extension option has a benefit/cost ratio of 1.63 for the urban system and 0.22 for the rural system. Thus, it is useful for the urban system but not for the rural system. The reason for this result is that the transformers in urban systems are larger in size and thus very expensive.
ECpE Department

## Slide 57: Thank You!
ECpE Department