## Slide 1: Microgrids (Part II) Microgrid Modeling and Control
EE 653 Power distribution system modeling, optimization and simulation
GRA: Zixiao Ma
Advisor: Dr. Zhaoyu Wang
Department of Electrical and Computer Engineering
Iowa State University

## Slide 2: Contents
Dynamic Modeling of Microgirds
  Background of Microgrids Modeling
  Mathematical Modeling of Inverter-Dominated Microgrids
  Reduced-Order Small-Signal Model of Inverter-Dominated Microgrids
Microgrids Control: Primary and Secondary
  Primary Control
    Active Load Sharing
    Droop Characteristic Techniques
    Discussion of Primary Control Level Techniques
  Secondary Control
    Literature Review of Secondary Control
    Distributed Cooperative Secondary Control of Microgrids Using Feedback Linearization

## Slide 3: Background of Microgrids Modeling
  Microgrids as the main building blocks of smart grids are small scale power systems that facilitate the effective integration of distributed energy resources (DERs).
  In normal operation, the microgrid is connected to the main grid. In the event of disturbances, the microgrid disconnects from the main grid and goes to the islanded operation.
  In the islanded mode operation of a microgrid, a part of the distributed network becomes electrically separated from the main grid, while loads are supported by local DERs. Such DERs are typically power electronic based, making the full system complex to study.
  A detailed mathematical model of microgrids is important for stability analysis, optimization, simulation studies and controller design.
Notes: What is MG???? Standard definisions

## Slide 4: Mathematical Model of Microgrid
Fig. 1. The diagram of VSI-based DER and controller block.
: the microgrid is operated in grid-tied mode
: the microgrid is operated in islanded mode

## Slide 5: Mathematical Model of Microgrid
Average Power Calculation: The generated active and reactive power can be calculated using the transformed output voltage and current . The average power generated by the inverter is
Using a low-pass filter (LPF) with the corner frequency we can obtain the filtered instantaneous powers as follows,
(1a)
(1b)
(2a)
(2b)
Fig. 2. The diagram power calculator.

## Slide 6: Mathematical Model of Microgrid
Phase Locked Loop: The phase lock loop (PLL) is used to measure the actual frequency of the system. According to [1], the PLL input is the d-axis component of the voltage measured across the filter capacitor (Fig. 4).
The mathematical model of PLL is represented as follows,
In grid-tied mode, the inverter output phase is synchronized to the main grid using PLL, therefore the derivative of phase angle is set to :
In islanded mode, the phase angle of the first inverter can be arbitrarily set as the reference for the other inverters:
(3a)
(3b)
(4)
(5)
Fig. 3. The diagram of PLL used for DER.
[1] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, “An accurate small-signal model of inverter-dominated islanded microgrids using dq reference frame,” IEEE J. Emerg. Sel. Topics Power Electron., vol. 2, no. 4, pp. 1070–1080, Dec. 2014.

## Slide 7
Power Controller: In grid-tied mode, the output power of DER is regulated by the power controller using PI control method. The input references are the commanded real and reactive powers:
(6a)
Fig. 4. The diagram of power controller PLL used for DER.
(6b)
(6c)
(6d)
Mathematical Model of Microgrid

## Slide 8
Droop Controllers: In grid-connected mode, the inverter’s output voltage is set by the grid voltage magnitude. The PLL ensures proper tracking of grid phase so that inverter output remains synchronized to the grid. In islanded mode, a DER has no reference inputs from the main grid. Therefore, it must generate its only voltage and frequency references using droop controllers as follows,
(7a)
(7b)
Fig. 5. Droop characteristic curves.
Mathematical Model of Microgrid

## Slide 9
Voltage Controllers: The reference frequency and voltage magnitude generated by the droop equations are used as set point values for the voltage controllers. Standard PI controllers are used for this purpose, as shown in Fig. 6. The process variables are the angular frequency from the PLL and the measured q-axis voltage ()
Fig. 6. The diagram of voltage controllers.
(8a)
(8b)
(8c)
(8d)
Mathematical Model of Microgrid

## Slide 10
Current Controllers: Another set of PI controllers are used for current controllers as shown in Fig.7. These controllers take the difference between the commanded filter inductor currents (), the measured filter inductor currents (), and produce commanded voltage values (). The values of correspond to the inverter output voltages before the LCL filter. Cross-coupling component terms are eliminated in these controllers as well
Fig. 7. The diagram of current controllers.
(9a)
(9b)
(9c)
(9d)
Mathematical Model of Microgrid

## Slide 11: Mathematical Model of Microgrid
LC Filters and Coupling Inductors: The filter in DER is shown in Fig. 8. Without any major inaccuracies, we can assume that the commanded voltage () appears at the input of the filter inductor, i.e., . This approach neglects only the losses in the IGBT and diodes. The state equations governing the filter dynamics are presented,
(10a)
(10b)
(10c)
(10d)
(10e)
(10f)
Fig. 8. The diagram of LCL filters.

## Slide 12
Load models: The loads for this system are chosen as combination of resistors and inductors (RL loads). A typical RL load connected to an inverter bus is shown in Fig. 9. Line ‘a’ connected to the bus represents the base load and line ‘b’ works as a variable load for that bus. To check the system’s dynamic behavior, a load perturbation is done on ‘b’. Line ‘b’ appears in parallel to ‘a’ when the breaker closes the contact. State equations describing the load dynamics are,
(11a)
(11b)
Fig. 9. Load configuration.
Mathematical Model of Microgrid

## Slide 13: Mathematical Model of Microgrid
Distribution line: Similar to loads, the distribution line parameters consist of resistance and inductance. In Fig. 10, resistor represents the copper loss component of the line. Inductor is considered as the lumped inductance resulting from long line cables. Assuming that the line is connected between th and th bus of the system, the line dynamics are represented as follows:
The frequency is constant throughout the system.
The variable subscript with upper case DQ denotes measurements from the global reference frame.
First inverter’s phase angle can be arbitrarily set as the reference for the entire system.
(12a)
(12b)
Fig. 10. Line configuration.

## Slide 14: Reference Frame Transformation
Inverter bus 1 serves as the system’s reference and consequently is labeled as the global reference frame. Each inverter operates in its own local reference frame. A transformation is necessary to translate between values defined in the local reference frame to the global reference frame. An application of this transformation is shown graphically in Fig. 11.
where θ is the difference between the global reference phase and the local reference phase, as shown in Fig. 12.
(13a)
(13b)
Fig. 11. Reference frame transformation.
Fig. 12. Transformation angle.

## Slide 15: State Space Model of Microgrid
The mathematical model of microgrid has been established as equation (1)-(13). We can represent this model in general state space equations as follows,
When the operation mode changes, the model structure switches as well. Therefore, we can define the state vectors in grid-tied () and islanded () modes, respectively.
,
.
The inputs are defined as
where is the number of inverters in microgrid.
(15a)
(15b)
(14)
(16)
Bus voltages
Control signal generated by secondary control

## Slide 16: Linearization of microgrid model
The above model is a nonlinear model. To simplify the problem, sometimes we need to obtain the small-signal model of microgrids. Let be an equilibrium of system (14), then we can take the Taylor Series expansion of around as follows,
where is the total order of microgrid, and is the number of inverters in the microgrid. Define the perturbation of states and inputs as , and .
Since is an equilibrium,
When the perturbation is small enough, we can neglect the high order terms.
Then we have
(17)
(18)

## Slide 17: Virtual Resistor Method
In the above model, bus voltages were used as an input to the system, thus, effects of load perturbation could not be accurately predicted.
However, in practice, the only perturbation that occurs in the system comes from the step change in load. A method is needed to include the terms relating to the bus voltages in the system matrix .
To do this, a virtual resistor with high resistance can be assumed connected at the inverter bus. This resistor (), shown in Fig. 13, has a negligible impact on system dynamics.
Using Kirchhoff’s voltage law (KVL), the equations describing the bus voltage in terms of the inverter, load currents and line currents can be expressed. This is shown in
(19a)
Fig. 13. Virtual resistor at a DER bus.
(19b)
(20a)
(20b)

## Slide 18: Model Order Reduction Method using Singular Perturbation
  Existing microgrid models have many state variables, thus increasing the computational burden and difficulty of stability analysis.
  The dynamical model exhibits behaviors at two time-scales: faster dynamics for converters and PI controllers; and slower dynamics for power calculator and droop controller.
  The reduced-order model is developed based on the singular perturbation theory that separates the system states into fast and slow dynamics.
Consider a singular perturbation model of a dynamical system whose derivatives of some of the states are multiplied by a small positive parameter ε (perturbation coefficient) as follows
where representing slower dynamics, representing faster dynamics. Let ε=0, we have
If G in (23) has at least one isolated real roots
(21)
(23)
(24)
(22)

## Slide 19: Model Order Reduction Method using Singular Perturbation
Substitute (24) into (21), we obtain the reduced order model as follows
Note that the dimension of (1) is reduced from n+m to n.
Compared to conventional order reduction that simply ignores some dynamic states, our method uses slower dynamics to represent faster ones, thus reducing order while maintaining all dynamic characteristics.
Even though we can get the reduced-order model using the above method, the accuracy of the reduced model is not guaranteed. Define a new time variable , and introduce the boundary-layer model as follows,
where 𝑦=𝑧−ℎ(𝑡,𝑥) is the change of state variables.
(25)
(26)

## Slide 20: Order Reduction Method for Small-Signal Microgrid Model
Then we can specify the singular perturbation theory for small-signal (linear) systems. First, we need to identify the slow and fast dynamics. For linear system, we can use the modal analysis by calculating the participation factor:
where and are left and right eigenvectors, respectively. Using the participation factor we can know that which eigenvalue participates mostly in which state. Then based on the magnitudes of their corresponding eigenvalues, we can determine the states with larger eigenvalues as fast states, while the others as slow states. For example,
(27)

## Slide 21: Order Reduction Method for Small-Signal Microgrid Model
The order reduction algorithm for small-signal microgrid model is given in the following steps [2]:
Discard (corresponding to the reference angle) by removing the corresponding row and column.
Rearrange the states of the original state vector such that the slow states are placed at the upper rows and fast states are placed at the lower rows. Use a transformation matrix for reordering. For example, needs to be reordered as . Use the transformation matrix to multiply the original vector. The new state vector and steady-state operating point vectors become and , respectively,
Find the new state matrix using : = .
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
(28)

## Slide 22: Order Reduction Method for Small-Signal Microgrid Model
Separate the new state matrix and the new states as follows:
where , , , . Also, is the representative of the slow states and is the representative of the fast states.
Perform the following iteration to find the value of L for a linear system composed of two subsystems [3]:
Start with the initial value and iterate 100 times. This will ensure that the eigenvalues of the reduced-order system are as close as possible to that of the slow eigenvalues of the full-order system. For this system, 100 iterations achieved excellent accuracy with minimal computational time.
[3] P. V. Kokotovic, “A Riccati equation for block-diagonalization of ill-conditioned systems,” IEEE Trans. Autom. Control, vol. 20, no. 6, pp. 812–814, Dec. 1975.
(29)
(30)
(31)
(32)

## Slide 23: Order Reduction Method for Small-Signal Microgrid Model
Transform the system into the following using the slow manifold condition :
where .
Perform the following iteration to find the value of :
Start with the initial value and iterate 100 times as before for .
Decouple the system into slow and fast time-scale using the fast manifold condition :
The operating points corresponding to the slow states become
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
(33)
(34)
(35)

## Slide 24: Order Reduction Method for Small-Signal Microgrid Model
To get the corrected response , add to the output of , where . New outputs are similar to that of the dynamics obtained from the slow states of the original system.
Predict the fast states using algebraic solutions
The reduced-order system is now ready for simulation. Fig. 14 shows the final arrangement for obtaining the dynamic response considering both the slow and the fast states.
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
Fig. 14. Corrected response from the reduced-order model.
(36)

## Slide 25: Simulation Validation of Small-Signal Order Reduction
Simulation setup: For the grid-tied system, a set of linearization points is obtained with to evaluate the initial higher order matrices in (12) as [2]. The parameter setting is given in TABLE I. Using modal analysis we can identify the slow/fast states as follows,
[1] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, “An accurate small-signal model of inverter-dominated islanded microgrids using dq reference frame,” IEEE J. Emerg. Sel. Topics Power Electron., vol. 2, no. 4, pp. 1070–1080, Dec. 2014.
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
Fig. 15. Two-bus microgrid system [1].
(37)
(38)

## Slide 26: Simulation Validation of Small-Signal Order Reduction
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
Fig. 16. Verification of the system dynamics of interests. (a) Active power. (b) Reactive power. (c) d-axis inductor current. (d) q-axis inductor current. (e) d-axis output current. (f) q-axis output current. (g) d-axis output voltage. (h) q-axis output voltage [2].

## Slide 27: Simulation Validation of Small-Signal Order Reduction
Simulation setup: For the islanded system, the equilibrium point and parameter setting is defined as [2]. The modal analysis result is shown in TABLE II.
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
TABLE II
EIGENVALUES OF SYSTEM MATRIX A
Fig. 17. Fast states marked with rectangles, are oscillatory in the full-order model but disappear in the reduced-order model and become straight lines.

## Slide 28: Simulation Validation of Small-Signal Order Reduction
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
Fig. 18 Verification of system dynamics using results from experiment, full-order model simulation, and reduced-order model simulation. (a) Active power. (b) Reactive power. (c) d-axis inductor current. (d) q-axis inductor current. (e) d-axis output current. (f) q-axis output current. (g) d-axis output voltage. (h) q-axis output voltage. [2].

## Slide 29
Microgrids control: Primary and Secondary
  Primary control
    Active Load Sharing
    Droop Characteristic Techniques
    Discussion of Primary Control Level Techniques
  Secondary control
    Literature Review of Secondary Control
    Distributed Cooperative Secondary Control of Microgrids Using Feedback Linearization
Microgrids Control: Primary and Secondary

## Slide 30
[4] A. Bidram and A. Davoudi, "Hierarchical Structure of Microgrids Control System," in IEEE Transactions on Smart Grid, vol. 3, no. 4, pp. 1963-1976, Dec. 2012.
Fig. 19 Hierarchical control levels of a MG [4]
Hierarchical Control of Microgrids
Primary control
  To stabilize the voltage and frequency. Subsequent to an islanding event, the MG may lose its voltage and frequency stability due to the mismatch between the power generated and consumed.
  To offer plug and play capability for DERs and properly share the active and reactive power among them, preferably, without any communication links.
  To provide the reference points for the control loops of DERs.
Secondary control
  As a centralized controller, secondary control restores the MG voltage and frequency and compensate for the deviations caused by the primary control.
  Secondary control is designed to have slower dynamics response than that of the primary.

## Slide 31
Fig. 20 Hierarchical control levels of a microgrid [4].
Hierarchical Control of Microgrids
[4] A. Bidram and A. Davoudi, "Hierarchical Structure of Microgrids Control System," in IEEE Transactions on Smart Grid, vol. 3, no. 4, pp. 1963-1976, Dec. 2012.

## Slide 32
Hierarchical Control of Microgrids
Primary control
The primary control is designed to satisfy the following requirements:
  To stabilize the voltage and frequency. Subsequent to an islanding event, the microgrid may lose its voltage and frequency stability due to the mismatch between the power generated and consumed.
  To offer plug and play capability for DERs and properly share the active and reactive power among them, preferably, without any communication links.
  To mitigate circulating currents that can cause over-current phenomenon in the power electronic devices and damage the DC-link capacitor.
  The primary control provides the reference points for the voltage and current control loops of DERs. These inner control loops are commonly referred to as zero-level control. The zero-level control is generally implemented in either PQ or voltage control modes

## Slide 33
Primary Control: PQ Control Mode
The control strategy is implemented with a current-controlled voltage source converter (VSC).
controller regulates the DC-link voltage and the active power through adjusting the magnitude of the output active current of the converter .
controller regulates the output reactive power by adjusting the magnitude of the output reactive current, i.e., [4].
[4] A. Bidram and A. Davoudi, "Hierarchical Structure of Microgrids Control System," in IEEE Transactions on Smart Grid, vol. 3, no. 4, pp. 1963-1976, Dec. 2012.
Fig. 21 PQ control mode with active and reactive power [4].

## Slide 34
Primary Control: Voltage Control Mode
The DER operates as a voltage-controlled VSC where the reference voltage, , is determined by the primary control, conventionally via droop characteristics, as shown in Fig. 22.
The nested voltage and frequency control loops in the voltage control mode are shown in Fig. 23. This controller feeds the current signal as a feedforward term via a transfer function (e.g., virtual impedance).
To fine-tune the transient response, proportional-integral-derivative (PID) [5], adaptive [6], and proportional resonant controllers [7] are proposed for the voltage controller.
[4] A. Bidram and A. Davoudi, "Hierarchical Structure of Microgrids Control System," in IEEE Transactions on Smart Grid, vol. 3, no. 4, pp. 1963-1976, Dec. 2012.
[5] M. J. Ryan, W. E. Brumsickle, and R. D. Lorenz, “Control topology options for single-phase UPS inverters,” IEEE Trans. Ind. Appl., vol. 33, pp. 493–501, Mar./Apr. 1997.
[6] G. Escobar, P. Mattavelli, A. M. Stankovic, A. A. Valdez, and J. L. Ramos, “An adaptive control for UPS to compensate unbalance and harmonic distortion using a combined capacitor/load current sensing,” IEEE Trans. Ind. Appl., vol. 54, pp. 839–847, Apr. 2007.
[7] A. Hasanzadeh, O. C. Onar, H. Mokhtari, and A. Khaligh, “A proportional-resonant controller-based wireless control strategy with a reduced number of sensors for parallel-operated UPSs,” IEEE Trans. Power Del., vol. 25, pp. 468–478, Jan. 2010.
Fig. 22 Reference voltage determination for voltage control mode [4].
Fig. 23 Voltage and current control loops in voltage control mode [4].

## Slide 35
Primary Control: Zero-Level Control
To improve the power quality for a set of energy sources connected to a common bus, the control structure shown in Fig. 24 is used.
Each converter has an independent current control loop, and a central voltage control loop that is adopted to distribute the fundamental component of the active and reactive powers among different sources.
The reference point for the voltage control loop is determined by the primary control.
The individual current controllers ensure power quality by controlling the harmonic contents of the supplied currents to the common AC bus.
[8] M. Prodanović and T. C. Green, “High-quality power generation through distributed control of a power park microgrid,” IEEE Trans. Ind. Electron., vol. 53, pp. 1471–1482, Oct. 2006.
Fig. 24 Zero-level control loops for a set of energy sources connected to an AC bus [8].

## Slide 36
Primary Control: Active Load Sharing
The active load sharing is a communication-based method used in parallel configuration of converters. Different approaches such as centralized, master-slave, average load sharing, and circular chain control methods [4].
In a centralized control method, the overall load current is evenly distributed among the sources by assigning the same current set points for all converters.
In the master-slave control, the master converter operates as a VSC and regulates the output voltage while the slave converters behave as individual current source converters that follow the current pattern of the master converter.
In the average load sharing control, the current reference for individual converters is continuously updated as the weighted average current of all converters (but not the load current).
In the circular chain control, converter modules are considered to be connected like links of a chain, and the current reference for each converter is determined by that of the previous converter.
The active load sharing method requires communication links and high bandwidth control loops. However, it offers precise current sharing and high power quality.
[4] A. Bidram and A. Davoudi, "Hierarchical Structure of Microgrids Control System," in IEEE Transactions on Smart Grid, vol. 3, no. 4, pp. 1963-1976, Dec. 2012.

## Slide 37
Primary Control: Droop Characteristic Techniques
The droop control method has been referred to as the independent, autonomous, and wireless control due to elimination of intercommunication links between the converters.
The conventional active power control (frequency droop characteristic) and reactive power control (voltage droop characteristic), those illustrated in Fig. 25, are used for voltage mode control.
Principles of the conventional droop methods can be explained by considering an equivalent circuit of a VSC connected to an AC bus, as shown in Fig. 7. If switching ripples and high frequency harmonics are neglected, the VSC can be modeled as an AC source, with the voltage of .
Fig. 25 Conventional droop method.
Fig. 26 Conventional droop method.

## Slide 38
Primary Control: Droop Characteristic Techniques
In addition, assume that the common AC bus voltage is and the converter output impedance and the line impedance are lumped as a single effective line impedance of . The complex power delivered to the common AC bus is calculated as
from which the real and reactive powers are achieved as
If the effective line impedance, , is assumed to be purely inductive, , then (40) can be reduced to
(39)
(40)
(41)

## Slide 39
Primary Control: Droop Characteristic Techniques
If the phase difference between the converter output voltage and the common AC bus, , is small enough, then, and . Thus, one can apply the frequency and voltage droop characteristics to fine-tune the voltage reference of the VSC, as shown in Fig. 25 based on
where and are the DER output voltage RMS value and angular frequency at the no-load, respectively. The droop coefficients, and , can be adjusted either heuristically or by tuning algorithms. In the former approach, and are determined based on the converter power rating and the maximum allowable voltage and frequency deviations. For instance, in a microgrid with DERs, corresponding and should satisfy following constraints
where and are the maximum allowable angular frequency and voltage deviations, respectively. and are the nominal active and reactive power of the th DER.
(42)
(43)

## Slide 40
Primary Control: Droop Characteristic Techniques
During the grid-tied operation of microgird, the DER voltage and angular frequency, and , are enforced by the gird. The DER output active and reactive power references, and , can hence be adjusted through and as
Dynamics response of the conventional primary control, on the simplified system of Fig. 26, can be studied by linearizing (40) and (41). For instance, the linearized active power equation in (40) and frequency droop characteristic in (41) are
where at the operating point of
(44)
(45)
(46)

## Slide 41
Primary Control: Droop Characteristic Techniques
Therefore, the small-signal model for the active power control in (42) is
A similar procedure can be adopted to extract the small-signal model of the reactive power control. The block diagram of the small-signal model for the active power control of (42) is demonstrated in Fig. 27. As seen in (47), time constant of the closed loop control can only be adjusted by tuning . On the other hand, as seen in (42), also affects the DER frequency. Thus, a basic trade-off exists between the time constant of the control system and the frequency regulation.
(47)
Fig. 27 Small-signal model of the conventional active power control.

## Slide 42
Discussion of Primary Control Level Techniques
As opposed to the active load sharing technique, the conventional droop method can be implemented with no communication links, and therefore, is more reliable. However, it has some drawbacks as listed below:
Since there is only one control variable for each droop characteristic, it is impossible to satisfy more than one control objectives. As an example, a design tradeoff needs to be considered between the time constant of the control system and the voltage and frequency regulation.
The conventional droop method is developed assuming highly inductive effective impedance between the VSC and the AC bus. However, this assumption is challenged in microgrid applications since low-voltage transmission lines are mainly resistive. Thus, (41) is not valid for microgrid applications [4].
As opposed to the frequency, the voltage is not a global quantity in the microgrid. Thus, the reactive power control in (42) may adversely affect the voltage regulation for critical loads [9].
In case of nonlinear loads, the conventional droop method is unable to distinguish the load current harmonics from the circulating current. Moreover, the current harmonics distorts the DER output voltage. The conventional droop method can be modified to reduce the total harmonic distortion (THD) of the output voltages.
[4] A. Bidram and A. Davoudi, "Hierarchical Structure of Microgrids Control System," in IEEE Transactions on Smart Grid, vol. 3, no. 4, pp. 1963-1976, Dec. 2012.
[9] E. Rokrok and M. E. H. Golshan, “Adaptive voltage droop method for voltage source converters in an islanded multibus microgrid,” IET Gen., Trans., Dist., vol. 4, no. 5, pp. 562–578, 2010.

## Slide 43
[10] M. C. Chandorkar, D. M. Divan, and R. Adapa, “Control of parallel connected inverters in standalone AC supply systems,” IEEE Trans. Ind. Appl., vol. 29, pp. 136–143, Jan./Feb. 1993.
[11] C. K. Sao and W. Lehn, “Autonomous load sharing of voltage source converters,” IEEE Trans. Power Del., vol. 20, pp. 1009–1016, Apr. 2005.
[12] C. K. Sao and W. Lehn, “Control and power management of converter fed microgrids,” IEEE Trans. Power Syst., vol. 23, pp. 1088–1098, Aug. 2008.
TABLE III
POTENTIAL ADVANTAGES AND DISADVANTAGES OF THE DISCUSSED DROOP METHODS
Droop Method | Potential advantages | Potential disadvantages
Conventional droop method [10] | Simple implementation | Affected by the system parameters. Only functional for highly inductive transmission lines. Cannot handle nonlinear loads. Voltage regulation is not guaranteed. Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls.
Adjustable load sharing method [11] | Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls. Robust to the system parameter variations. Improved voltage regulation. | Cannot handle nonlinear loads.
VPD/FQB droop method [12] | Simple implementation Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls. | Affected by the system parameters. Only functional for highly inductive transmission lines. Cannot handle nonlinear loads.
Discussion of Primary Control Level Techniques

## Slide 44
Virtual frame transformation method [13] | Simple implementation. Decoupled active and reactive power controls. | Cannot handle nonlinear loads. The line impedances should be known a priori. Voltage regulation is not guaranteed. Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls.
Virtual output impedance [14] | Simple implementation. Not affected by the system parameters. Functional for both linear and nonlinear loads. Mitigates the harmonic distortion of the output voltage. Can compensate for the unbalance of the DER output voltages. | Voltage regulation is not guaranteed. Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls.
Adaptive voltage droop method [15] | Improved voltage regulation. Not affected by the system parameters. | Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls. Cannot handle nonlinear loads. System parameters should be known a priori.
Signal injection method [16] | Functional for both linear and nonlinear loads. Not affected by the system parameters. | Complicated implementation. Voltage regulation is not guaranteed. Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls.
Nonlinear load sharing techniques [17] | Properly shares the current harmonics between the DERs, and consequently, cancels out the voltage harmonics. | Adjusting the controller speed for the active and reactive power controllers can affect the voltage and frequency controls. Poor voltage regulation for the case of precise reactive power sharing. Affected by the system parameters.
Discussion of Primary Control Level Techniques

## Slide 45
Secondary Control of Microgrids
Secondary control
The primary control is designed to satisfy the following requirements:
  As a centralized controller, secondary control restores the MG voltage and frequency and compensate for the deviations caused by the primary control.
  Secondary control is designed to have slower dynamics response than that of the primary.
  Primary control, as discussed, may cause frequency deviation even in steady state. Although the storage devices can compensate for this deviation, they are unable to provide the power for load-frequency control in long terms due to their short energy capacity. The secondary control, as a centralized controller, restores the microgrid voltage and frequency and compensate for the deviations caused by the primary control. This control hierarchy is designed to have slower dynamics response than that of the primary, which justifies the decoupled dynamics of the primary and the secondary control loops and facilitates their individual designs.

## Slide 46
Differences and Connections between Primary and Secondary Control
 | Differences | Connections
Primary Control | Operated in faster time-scale Aims to stabilize the voltage and frequency Cannot eliminate steady-state errors Distributed local controllers | The input reference of primary control is the control signal generated by secondary control Since primary control has steady-state errors, the output of primary level is fed back to the secondary control as the output feedback. Then, the secondary level designs control law to realize accurate output tracking by minimizing the error between output feedback and desired values. When designing secondary controller, the primary controlled microgrid is viewed as a plant of secondary control.
Secondary Control | Operated in slower time-scale Aims to restore the voltage and frequency to their reference values Can eliminate steady-state errors Can be centralized, decentralized or distributed. | 
TABLE IV
DIFFERENCES AND CONNECTIONS BETWEEN PRIMARY AND SECONDARY CONTROL

## Slide 47
Conventional Secondary and Primary Control structure of Microgrids
[18] A. Bidram, et al. "Secondary control of microgrids based on distributed cooperative control of multi-agent systems." IET Generation, Transmission & Distribution 7.8 (2013): 822-831.
Fig. 28 Conventional control levels of a microgrid [5]

## Slide 48
Existing Secondary Control Methods of Microgrids
TABLE V
SECONDARY CONTROL METHODS OF MICROGRIDS
Secondary control | Centralized | PID | Simple implementation. Cannot realize accurate output regulation.
 |  | Potential function-based optimization | Optimal control objectives. Requires bidirectional communication infrastructure.
 |  | Voltage unbalance compensation | Satisfy the power quality requirements.
 |  | Feedback linearization | Simple implementation for nonlinear systems. Require accurate mathematical models.
 | Decentralized | Adaptive control | Robust to the system parameter variations. Can be extended to model-free control. Do not need communication infrastructure.
 | Distributed | Distributed feedback linearization | Improved reliability. Simple implementation for nonlinear systems. Require accurate mathematical models.
 |  | Distributed adaptive control | Robust to the system parameter variations. Can be extended to model-free control. Improved reliability.
 |  | Distributed model predictive control | Optimal control objectives. Rolling closed-loop control. Can deal with constraints.

## Slide 49
Secondary Control: PID Control
When using PI controller in secondary control, frequency of the microgrid and the terminal voltage of a given DER are compared with the corresponding reference values, and , respectively. Then, the error signals are processed by individual controllers as in (48); the resulting signals ( and ) are sent to the primary controller of the DER to compensate for the frequency and voltage deviations
where and are the controllers parameters. An additional term, , is considered in frequency controller in (48) to facilitate synchronization of the microgird to the main gird. In the islanded operating mode, this additional term is zero. However, during the synchronization, a PLL module is required to measure . During the grid-tied operation, voltage and frequency of the main grid are considered as the references in (48).
(48)

## Slide 50
Secondary Control: Potential function-based Control
Most recently, potential function-based optimization technique has been suggested for the secondary control [19]. In this method, a potential function is considered for each DER. The block diagram of the potential function-based technique is shown in Fig. 29. In this technique, when the potential functions approach their minimum values, the microgrid is about to operate at the desired states. Therefore, inside the optimizer in Fig. 29, set points of the DER are determined such that to minimize the potential functions, and thus, to meet the microgrid control objectives.
Fig. 29 The potential function-based technique block diagram [19].
[19] F. Katiraei, M. R. Iravani, and P. W. Lehn, “Microgrid autonomous operation during and subsequent to islanding process,” IEEE Trans. Power Del., vol. 20, pp. 248–257, Jan. 2005.

## Slide 51
Secondary Control: Potential function-based Control
In this method, a potential function is considered for each DER [19]. This function is a scalar cost function that carries all the information on the DER measurements, constraints, and control objectives as
where is the potential function related to each DER, and comprises the measurements from the DER unit (e.g., voltage, current, real and reactive power). denotes the partial potential functions that reflect the measurement information of the DER. denotes the operation constraints that ensure the stable operation of microgrid. is used to mitigate the DER measurements from the pre-defined set points. are the weighted factors for the partial potential functions.
(49)
[19] F. Katiraei, M. R. Iravani, and P. W. Lehn, “Microgrid autonomous operation during and subsequent to islanding process,” IEEE Trans. Power Del., vol. 20, pp. 248–257, Jan. 2005.

## Slide 52
Distributed Secondary Control: Graph Theory
The communication network of a multiagent cooperative system can be modeled by a directed graph (digraph). A digraph is expressed as with a nonempty finite set of nodes , a set of edges or arcs, and the associated adjacency matrix In a microgrid, DGs are the nodes of the communication digraph. The edges of the corresponding digraph of the communication network represent the communication links [20].
An edge from node to node is denoted by , which means that node receives the information from node . is the weight of edge and if , otherwise . Node is called a neighbor of node if . The set of neighbors of node is denoted as . For a digraph, if node is a neighbor of node , then node can get information from node but not necessarily vice versa. The in-degree matrix is defined as with . The Laplacian matrix is defined as . A directed path from node to node is a sequence of edges, expressed as .
A digraph is said to have a spanning tree if there is a root node with a directed path from that node to every other node in the graph. A digraph is strongly connected if there is a directed path between any two nodes in the graph.
[20] A. Bidram, F. L. Lewis and A. Davoudi, "Distributed Control Systems for Small-Scale Power Networks: Using Multiagent Cooperative Control Theory," in IEEE Control Systems Magazine, vol. 34, no. 6, pp. 56-77, Dec. 2014.

## Slide 53
Distributed Secondary Voltage Control: Feedback linearization
Recall the large-signal dynamic model of microgrid, we can rewrite it in the following control-affine form:
where , , , , can be extracted from (1)-(13).
Input–output feedback linearization can be used to facilitate the secondary voltage control design. In input–output feedback linearization, a direct relationship between the dynamics of the output and the control input is generated by repetitively differentiating with respect to time.
For the dynamics of the th DG in (50), the direct relationship between the and is generated after the second derivative of the output ,
where
(50)
(51)
(52)

## Slide 54
Distributed Secondary Voltage Control: Feedback linearization
The Lie derivative with respect to is defined as
An auxiliary control is defined as
Equations (51) and (55) result in the second-order linear system
By choosing appropriate , the synchronization for is provided. The control input is implemented by as
To design , first (56) and the first derivative of are written as
where is defined as the first derivative of .
(53)
(56)
(57)
(54)
(55)
(58)

## Slide 55
Distributed Secondary Voltage Control: Feedback linearization
The compact form of (58) can be written as
where , and .
The commensurate reformulated dynamics of the reference can be expressed as
where Since is constant,
It is assumed that DGs can communicate with each other through a communication network described by the digraph . Based on the digraph , the th DG may need to transmit in (59) through the communication network. It is assumed that only one DG has access to the reference in (60) by a weight factor known as the pinning gain . The secondary voltage control problem is to find a distributed in (57) such that DG output voltage magnitudes and their first derivatives synchronize to in (60), that is, synchronizes for all .
(59)
(60)

## Slide 56
Distributed Secondary Voltage Control: Feedback linearization
To solve this problem, the cooperative team objectives are expressed in terms of the local neighborhood tracking error
where denotes the set of DGs neighboring the th DG, and denotes the elements of the communication digraph adjacency matrix. The pinning gain is nonzero for only one DG. For a microgrid including DGs, the global error vector for graph is written from (61) as
where (is the vector of ones with the length of ), , is the identity matrix, is the global disagreement vector, denotes the Kronecker product, then it follows that
where is the global auxiliary control vector, and can be written as
(61)
(62)
(63)
(64)

## Slide 57
Distributed Secondary Voltage Control: Feedback linearization
Let the digraph have a spanning tree and for one DG placed on a root node of the digraph Gr. It is assumed that the internal dynamics of each DG are asymptotically stable. Let the auxiliary control in (57) be
where is the coupling gain and is the feedback control vector. Then, all in (59) synchronize to in (60) and hence the direct term of DG output voltages synchronizes to , if the feedback gain is chosen as
where is the unique positive-definite solution of the control algebraic Riccati equation (ARE)
and
where , where are the eigenvalues of
(65)
(66)
(67)
(68)

## Slide 58
Distributed Secondary Voltage Control: Feedback linearization
Fig. 30 The block diagram of the proposed secondary voltage control. The secondary voltage control at each distributed generator (DG) only requires its own and neighboring DGs’ terminal voltage amplitude and first derivative [20].

## Slide 59
Distributed Secondary Voltage Control: Feedback linearization
Fig. 33 DG output voltage magnitudes for Case B: (a) when p.u., (b) when p.u., and (c) when p.u.. [20].
Fig. 32 Topology of the communication digraph.
Fig. 31 Single-line diagram of the microgrid test system.
[20] A. Bidram, F. L. Lewis and A. Davoudi, "Distributed Control Systems for Small-Scale Power Networks: Using Multiagent Cooperative Control Theory," in IEEE Control Systems Magazine, vol. 34, no. 6, pp. 56-77, Dec. 2014.

## Slide 60
Distributed Secondary Frequency Control: Feedback linearization
The secondary frequency control is similar to that of voltage control. The primary frequency control is considered,
where is the primary frequency control reference and Dpi is the frequency-active power droop coefficient. The secondary frequency control chooses such that the angular frequency of each DG, , synchronizes to the nominal angular frequency, , that is, or rad/s. Once the secondary frequency control is applied, the DG output powers are allocated according to the same pattern used for primary control.
Differentiating the frequency-droop characteristic in (69) yields
The auxiliary controls are chosen as
where is the coupling gain. It is assumed that the pinning gain is nonzero for only one DG that has the reference frequency .
(69)
(70)
(71)

## Slide 61
Distributed Secondary Frequency Control: Feedback linearization
Fig. 34 The block diagram of the distributed secondary frequency control. The secondary frequency control at each distributed generator (DG) only requires its own frequency and active power, and the frequency and active power of neighboring DGs on the communication network. [20].
The block diagram of the secondary frequency control based on the distributed cooperative control is shown in Figure 12. As seen in this figure, the control input to the primary control level is
(72)

## Slide 62: References
[1] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, “An accurate small-signal model of inverter-dominated islanded microgrids using dq reference frame,” IEEE J. Emerg. Sel. Topics Power Electron., vol. 2, no. 4, pp. 1070–1080, Dec. 2014.
[2] M. Rasheduzzaman, J. A. Mueller, and J. W. Kimball, Rasheduzzaman. "Reduced-order small-signal model of microgrid systems." IEEE Transactions on Sustainable Energy 6.4 (2015): 1292-1305.
[3] P. V. Kokotovic, “A Riccati equation for block-diagonalization of ill-conditioned systems,” IEEE Trans. Autom. Control, vol. 20, no. 6, pp. 812–814, Dec. 1975. [4] A. Bidram and A. Davoudi, "Hierarchical Structure of Microgrids Control System," in IEEE Transactions on Smart Grid, vol. 3, no. 4, pp. 1963-1976, Dec. 2012.
[5] M. J. Ryan, W. E. Brumsickle, and R. D. Lorenz, “Control topology options for single-phase UPS inverters,” IEEE Trans. Ind. Appl., vol. 33, pp. 493–501, Mar./Apr. 1997.
[6] G. Escobar, P. Mattavelli, A. M. Stankovic, A. A. Valdez, and J. L. Ramos, “An adaptive control for UPS to compensate unbalance and harmonic distortion using a combined capacitor/load current sensing,” IEEE Trans. Ind. Appl., vol. 54, pp. 839–847, Apr. 2007.
[7] A. Hasanzadeh, O. C. Onar, H. Mokhtari, and A. Khaligh, “A proportional-resonant controller-based wireless control strategy with a reduced number of sensors for parallel-operated UPSs,” IEEE Trans. Power Del., vol. 25, pp. 468–478, Jan. 2010.
[8] M. Prodanović and T. C. Green, “High-quality power generation through distributed control of a power park microgrid,” IEEE Trans. Ind. Electron., vol. 53, pp. 1471–1482, Oct. 2006.
[9] E. Rokrok and M. E. H. Golshan, “Adaptive voltage droop method for voltage source converters in an islanded multibus microgrid,” IET Gen., Trans., Dist., vol. 4, no. 5, pp. 562–578, 2010.
[10] M. C. Chandorkar, D. M. Divan, and R. Adapa, “Control of parallel connected inverters in standalone AC supply systems,” IEEE Trans. Ind. Appl., vol. 29, pp. 136–143, Jan./Feb. 1993.
[11] C. K. Sao and W. Lehn, “Autonomous load sharing of voltage source converters,” IEEE Trans. Power Del., vol. 20, pp. 1009–1016, Apr. 2005.

## Slide 63: References
[12] C. K. Sao and W. Lehn, “Control and power management of converter fed microgrids,” IEEE Trans. Power Syst., vol. 23, pp. 1088–1098, Aug. 2008.
[13] Y. Li and Y. W. Li, “Power management of inverter interfaced autonomous microgrid based on virtual frequency-voltage frame,” IEEE Trans. Smart Grid, vol. 2, pp. 30–40, Mar. 2011.
[14] W. Yao,M. Chen, J. Matas, J. M. Guerrero, and Z. Qian, “Design and analysis of the droop control method for parallel inverters considering the impact of the complex impedance on the power sharing,” IEEE Trans. Ind. Electron., vol. 58, pp. 576–588, Feb. 2011.
[15] J. M. Guerrero, L. G. D. Vicuna, J. Matas, M. Castilla, and J. Miret, “Output impedance design of parallel-connected UPS inverters with wireless load-sharing control,” IEEE Trans. Ind. Electron., vol. 52, pp. 1126–1135, Aug. 2005.
[16] A. Tuladhar, H. Jin, T. Unger, and K. Mauch, “Control of parallel inverters in distributed AC power systems with consideration of line impedance effect,” IEEE Trans. Ind. Appl., vol. 36, pp. 131–138, Jan./Feb. 2000.
[17] U. Borup, F. Blaabjerg, and P. N. Enjeti, “Sharing of nonlinear load in parallel-connected three-phase converters,” IEEE Trans. Ind. Appl., vol. 37, pp. 1817–1823, Nov./Dec. 2001.
[18] A. Bidram, et al. "Secondary control of microgrids based on distributed cooperative control of multi-agent systems." IET Generation, Transmission & Distribution 7.8 (2013): 822-831.
[19] F. Katiraei, M. R. Iravani, and P. W. Lehn, “Microgrid autonomous operation during and subsequent to islanding process,” IEEE Trans. Power Del., vol. 20, pp. 248–257, Jan. 2005.
[20] A. Bidram, F. L. Lewis and A. Davoudi, "Distributed Control Systems for Small-Scale Power Networks: Using Multiagent Cooperative Control Theory," in IEEE Control Systems Magazine, vol. 34, no. 6, pp. 56-77, Dec. 2014.

## Slide 64: Thank you!