## Slide 1: EE653 Power distribution system modeling, optimization and simulation
Dr. Zhaoyu Wang
1113 Coover Hall, Ames, IA
wzy@iastate.edu
ECpE Department

## Slide 2: Nature of Loads
ECpE Department
Acknowledgement: The slides are developed based in part on Distribution System Modeling and Analysis, 4th edition, William H. Kersting, CRC Press, 2017

## Slide 3
In order to describe the changing load, the following terms are defined:
1. Demand
  a. Load averaged over a specific period of time
  b. Load can be kW, kvar, kVA, or VA
  c. Must include the time interval
  d. Example: The 15 min kW demand is 100 kW
2. Maximum demand
  a. Greatest of all demands that occur during a specific time
  b. Must include demand interval, period, and units
  c. Example: The 15 min maximum kW demand for the week was 150 kW
3. Average demand
  a. The average of the demands over a specified period (day, week, month, etc.)
  b. Must include demand interval, period, and units
  c. Example: The 15 min average kW demand for the month was 350 kW
Definitions
ECpE Department

## Slide 4
4. Diversified demand
  a. Sum of demands imposed by a group of loads over a particular period
  b. Must include demand interval, period, and units
  c. Example: The 15 min diversified kW demand in the period ending at 9:30 was 200 kW
5. Maximum diversified demand
  a. Maximum of the sum of the demands imposed by a group of loads over a particular period
  b. Must include demand interval, period, and units
  Example: The 15 min maximum diversified kW demand for the week was 500 kW
6. Maximum noncoincident demand
  a. For a group of loads, the sum of the individual maximum demands without any restriction that they occur at the same time
  b. Must include demand interval, period, and units
  c. Example: The maximum noncoincident 15 min kW demand for the week was 700 kW
7. Demand factor
  a. Ratio of maximum demand to connected load
Definitions
ECpE Department

## Slide 5
8. Utilization factor
  a. Ratio of the maximum demand to rated capacity
9. Load factor
  a. Ratio of the average demand of any individual customer or a group of customers over a period to the maximum demand over the same period
10. Diversity factor
  a. Ratio of the “maximum noncoincident demand” to the “maximum diversified demand”
11. Load diversity
  a. Difference between “maximum noncoincident demand” and the “maximum diversified demand”
Definitions
ECpE Department

## Slide 6
The demand curve is broken into equal time intervals. In Fig.1, the selected time interval is 15 min. In each interval, the average value of the demand is determined. The straight lines represent the average load in a time interval. The shorter the time interval, the more accurate will be the value of the load.
Fig.1 Customer demand curve
Individual Customer Load
ECpE Department

## Slide 7
Calculate: 1) maximum demand; 2) Average demand; 3) Energy usage (total kWh); 4) Load factor
For this customer, the “15 min maximum kW demand” occurs at 13:15 and has a value of 6.18 kW.
Individual Customer Load
Fig.2 24-hour demand curve for customer#1 (from AMI, notice 15 min. incr.)
ECpE Department

## Slide 8
During the 24 h period, energy (kWh) will be consumed. The energy in kWh used during each 15 min time interval is computed by:
Individual Customer Load
Fig.2 24-hour demand curve for customer#1 (from AMI, notice 15 min. incr.)
Sum these over the time period.
kWh
ECpE Department

## Slide 9
The total energy consumed during the day is the summation of all of the 15 min interval consumptions. The total energy consumed during the period by customer #1 is 58.96 kWh. The “15 min average kW demand” is computed
Individual Customer Load
Fig.2 24-hour demand curve for customer#1 (from AMI, notice 15 min. incr.)
Average_demand
ECpE Department
Notes: Or 15min⁡_kW_demand/96

## Slide 10
“Load factor” is a term that is often referred to when describing a load. It is defined as the ratio of the average demand to the maximum demand. In many ways, load factor gives an indication of how well the utility's facilities are being utilized. From the utility's standpoint, the optimal load factor would be 1.00 since the system has to be designed to handle the maximum demand. Sometimes utility companies will encourage industrial customers to improve their load factor. One method of encouragement is to penalize the customer on the electric bill for having a low load factor.
Individual Customer Load
Fig.2 24-hour demand curve for customer#1 (from AMI, notice 15 min. incr.)
ECpE Department

## Slide 11
For customer #1 in Fig.2 the load factor is computed to be
Individual Customer Load
Fig.2 24-hour demand curve for customer#1 (from AMI, notice 15 min. incr.)
Load_f
System capacity must meet maximum demand.
Ideal load factor is 1.0.
ECpE Department

## Slide 12
Distribution Transformer Loading
Fig.2 24-hour demand curve for customer#1
Fig.3 24-hour demand curve for customer#2
Fig.4 24-hour demand curve for customer#3
Fig.5 24-hour demand curve for customer#4
ECpE Department

## Slide 13
Distribution Transformer Loading
Table 1 Individual Customer Load Characteristics
A distribution transformer will provide service to one or more customers. Each customer will have a demand curve similar to that of Fig. 2. However, the peaks and valleys and maximum demands will be different for each customer.
The load curves for the four customers show that each customer has its unique loading characteristic. The customers’ individual maximum kW demand occurs at different times of the day. Customer #3 is the only customer who will have a high load factor. A summary of individual loads is given in Table 1. The four customers given in Table 1 demonstrate that there is great diversity between their loads.
ECpE Department

## Slide 14
Diversified Demand
Fig.6 Transformer diversified demand curve
The sum of the four 15 kW demands for each time interval is the “diversified demand” for the group in that time interval, and in this case, the distribution transformer. The 15 min diversified kW demand of the transformer for the day is shown in Fig.6
Maximum Diversified Demand: It occurs at 17:30 and has a value of 16.16 kW.
ECpE Department

## Slide 15
Fig.2 24-hour demand curve for customer#1
Fig.3 24-hour demand curve for customer#2
Fig.4 24-hour demand curve for customer#3
Fig.5 24-hour demand curve for customer#4
M
The “15 min maximum noncoincident kW demand” for the day is the sum of the individual customer 15 min maximum kW demands. For the transformer in question, the sum of the individual maximums
Maximum Noncoincident Demand
ECpE Department

## Slide 16
M
By definition, diversity factor (DF) is the ratio of the maximum noncoincident demand of a group of customers to the maximum diversified demand of the group. With reference to the transformer serving four customers, the DF for the four customers would be:
Diversity Factor
Diversity_f=
Fig.2 24-hour demand curve for customer#1
Fig.3 24-hour demand curve for customer#2
Fig.4 24-hour demand curve for customer#3
Fig.5 24-hour demand curve for customer#4
ECpE Department

## Slide 17
Table 2 is an example of the DFs for the number of customers ranging from 1 up to 70. The table was developed from a different database than the four customers that have been discussed previously.
Diversity Factor
Table 2 Diversity Factors
ECpE Department

## Slide 18
A graph of the DFs is shown in Fig.8.
Diversity Factor
Fig.8 Diversity Factor
Note that, in Table 2 and Fig. 8, the value of the DF basically leveled out when the number of customers reached 70. This is an important observation because it means, at least for the system from which these DFs were determined, that the DF will remain constant at 3.20 from 70 customers and above. In other words as viewed from the substation, the maximum diversified demand of a feeder can be predicted by computing the total noncoincident maximum demand of all of the customers served by the feeder and dividing by 3.2.
ECpE Department

## Slide 19
This is for individual customers. We may be able
to total up demand for all connected appliances and
then apply demand factor to estimate peak demand
of the customer.
Customer #1
Peak demand is 6.18 kW.
Assume total connected load is 35kW.
Demand_f
Demand Factor
ECpE Department

## Slide 20
Utilization_f
Utilization Factor
The utilization factor gives an indication of how well the capacity of an electrical device is being utilized. For example, the transformer serving the four loads is rated 15 kVA. Using the 16.16 kW maximum diversified demand and assuming a power factor of 0.9, the 15 min maximum kVA demand on the transformer is computed by dividing the 16.16 kW maximum kW demand by the power factor and would be 17.96 kVA. The utilization factor is computed to be:
ECpE Department

## Slide 21
Load Diversity
Load diversity is defined as the difference between the noncoincident maximum demand and the maximum diversified demand
For our example transformer with 4 customers:
Load_Diversity
ECpE Department

## Slide 22
Feeder Load
Fig.9 Feeder demand curve
In the analysis of a distribution feeder, “load” data will have to be specified. The data provided will depend upon how detailed the feeder is to be modeled and the availability of customer load data. The most comprehensive model of a feeder will represent every distribution transformer. When this is the case, the load allocated to each transformer needs to be determined.
ECpE Department

## Slide 23
Application of Diversity Factors
The definition of the DF is the ratio of the maximum noncoincident demand to the maximum diversified demand. DFs are shown in Table 2. When such a table is available, then it is possible to determine the maximum diversified demand of a group of customers such as those served by a distribution transformer. That is, the maximum diversified demand can be computed by:
Diversity_f
ECpE Department

## Slide 24
But how could we know peak demand? (w/o demand mtr)
Many times the maximum demand of individual customers will be known either from metering or from knowledge of the energy (kWh) consumed by the customer. Some utility companies will perform a load survey of similar customers in order to determine the relationship between the energy consumption in kWh and the maximum kW demand. Such a load survey requires the installation of a demand meter at each customer's location.
Relate energy consumption to peak demand through study:
Similar type of customers (residential)
Metering on each customer for study
The plot of points for 15 customers along with the resulting equation derived
Fig.10 kW demand versus kWh for residential customers
ECpE Department

## Slide 25: Example 1
Analyze a single phase lateral.
Lateral means “to the side” like a lateral pass.
Want to know voltages and flows.
We just know energy usage for each customer (kWh).
Fig.11 Single-phase lateral
ECpE Department

## Slide 26: Example 1
A single-phase lateral provides service to three distribution transformers as shown in Fig.11.
The energy in kWh consumed by each customer during a month is known. A load survey has been conducted for customers in this class, and it has been found that the customer 15 min maximum kW demand is given by the equation
*
The kWh consumed by customer #1 is 1523 kWh. The 15 min maximum kW demand for customer #1 is then computed as
ECpE Department

## Slide 27: Example 1
Transformer T1
Transformer T2
Transformer T3
The results of this calculation for the remainder of the customers are summarized in the following table by transformer
ECpE Department

## Slide 28: Example 1
Q1: Determine for each transformer the 15 min noncoincident maximum kW demand, and using the DFs in Table 2, determine the 15 min maximum diversified kW demand.
Q2: Determine the 15 min noncoincident maximum kW demand and 15 min maximum diversified kW demand for each of the line segments
Tab.2 Diversity Factors
ECpE Department

## Slide 29: Example 1
Q1: Determine for each transformer the 15 min noncoincident maximum kW demand, and using the DFs in Tab.2, determine the 15 min maximum diversified kW demand.
T1: Noncoin._max. = 12.4 + 13.4 + 16.1 + 12.9 + 11.9 = 66.7kW
Max._div._d
T2: Noncoin._max. = 12.9 + 13.8 + 14.2 + 16.3 + 14.3 + 17.0 = 81.6kW
Max._div._d
T3: Noncoin._max. = 17.0 + 15.1 + 16.7 + 18.3 + 17.3 + 16.1 + 17.0 = 117.5kW
Max._div._d
ECpE Department

## Slide 30: Example 1
What size should the transformers be?
Choose from 25, 37.5, or 50 kVA.
Based upon the 15 min maximum kW diversified demand on each transformer and an assumed power factor of 0.9, the 15 min maximum kVA diversified demand on each transformer would be
Max._kVA._d
Max._kVA._d
Max._kVA._d
The kVA ratings selected for the three transformers would be 25, 37.5, and 50 kVA, respectively. With those selections, only transformer T1 would experience a significant maximum kVA demand greater than its rating (135%).
ECpE Department

## Slide 31: Example 1
Q2: Determine the 15 min noncoincident maximum kW demand and 15 min maximum diversified kW demand for each of the line segments
Segment N1 to N2:
The maximum noncoincident kW demand is the sum of the maximum demands of all 18 customers.
Noncoin._max._d
The maximum diversified kW demand is computed by using the DF for 18 customers
Max._div._d
ECpE Department

## Slide 32: Example 1
Q2: Determine the 15 min noncoincident maximum kW demand and 15 min maximum diversified kW demand for each of the line segments
Segment N2 to N3:
This line segment “sees” 13 customers. The noncoincident maximum demand is the sum of customer numbers 6 through 18. The DF for 13 (2.74) is used to compute the maximum diversified kW demand.
Noncoin._d
Max._div._d
ECpE Department

## Slide 33: Example 1
Q2: Determine the 15 min noncoincident maximum kW demand and 15 min maximum diversified kW demand for each of the line segments
Segment N3 to N4:
This line segment “sees” the same noncoincident demand and diversified demand as that of transformer T3.
Noncoin._d
Max._div._d
ECpE Department

## Slide 34
Transformer load management:
If we know which customers are connected
to which transformer, we can estimate the
xfmr max. diversified demand to check for
overloaded transformers.
Prevent transformer failures
Prevent transformer fires
Better usage of capital (money)
ECpE Department

## Slide 35
Another Approach - Allocation Factor
(top down):
What if we know
The peak demand for the whole feeder
The apparent power rating of all the
transformers connected to the feeder.
where
Metered_demand can be either kW or kVA
kVAtotal is the sum of the kVA ratings of all distribution transformers
The allocated load per transformer is then determined by
ECpE Department

## Slide 36: Example 2
Assume that the metered maximum diversified kW demand for the system of Example 2.1 is 92.9 kW. Allocate this load according to the kVA ratings of the three transformers.
kVA_total
A
The allocated kW for each transformer
T1:kW
T2:kW
T3:kW
ECpE Department

## Slide 37
Voltage Drop Calculations Using
Allocated Loads
Will use two allocation methods:
Diversity Factors – bottom up approach
Allocation factor – when substation metering data available
ECpE Department

## Slide 38: Example 3
For the system of Example 2.1, assume the voltage at N1 is 2400 V and compute the secondary voltages on the three transformers using the DFs.
The system of Example 2.1 including segment distances is shown in following figure.
Assume that the power factor of the loads is 0.9 lagging.
The impedance of the lines are z = 0.3 + j0.6 Ω/mile
The rating of the transformers are as follows:
T1:25 kV
T2:37.5 kV
T3:50 kV
ECpE Department

## Slide 39: Example 3
For the system of Example 2.1, assume the voltage at N1 is 2400 V and compute the secondary voltages on the three transformers using the DFs.
The system of Example 2.1 including segment distances is shown in following figure.
Assume that the power factor of the loads is 0.9 lagging.
The impedance of the lines are z = 0.3 + j0.6 Ω/mile
From Example 2.1 the maximum diversified kW demands were computed. Using the 0.9 lagging power factor, the maximum diversified kW and kVA demands for the line segments and transformers
Segment N1-N2:
Segment N2-N3:
Segment N3-N4:
Transformer T1:
Transformer T2:
Transformer T3:
ECpE Department

## Slide 40: Example 3
Convert transformer impedances to Ohms referred to the high voltage side
T
T
T
Compute the line impedances:
N
N
N
ECpE Department

## Slide 41: Example 3
Calculate the current flowing in segment N1–N2:
25.84 A
Calculate the voltage at N2:
.4 V
.8 V
Calculate the current flowing into T1:
26.24 A
Calculate the secondary voltage referred to the high side:
ECpE Department

## Slide 42: Example 3
Compute the secondary voltage by dividing by the turns ratio of 10:
0.8 V
Calculate the current flowing in line section N3–N4:
Calculate the voltage at N4:
0.4(0.0426+0.0852)*22.9 26.27=2375.0 0.5 V
The current flowing into T3 is the same as the current from N3 to N4:
Calculate the secondary voltage referred to the high side：

## Slide 43: Example 3
Compute the secondary voltage by dividing by the turns ratio of 10:
1.0 V
Calculate the percent voltage drop to the secondary of transformer T3. Use the secondary voltage referred to the high side：
=3.0789%
ECpE Department

## Slide 44: Example 4
For the system of Example 2.1, assume the voltage at N1 is 2400 V, and compute the secondary voltages on the three transformers, allocating the loads based upon the transformer ratings. Assume that the metered kW demand at N1 is 92.9 kW.
The impedances of the line segments and transformers are the same as in Example 2.3.
Assume the load power factor is 0.9 lagging, and compute the kVA demand at N1 from the metered demand：
kVA
Calculate the AF:
ECpE Department

## Slide 45: Example 4
Allocate the loads to each transformer:
Calculate the line flows:
kVA
)*25=20.6+j10.0 kVA
)*37.5=31.0+j15.0 kVA
)*50=41.3+j20.0 kVA
kVA
kVA
ECpE Department

## Slide 46: Example 4
The percent voltage drop for this case is
=2.7179%
Using these values of line flows and flows into transformers, the procedure for computing the transformer secondary voltages is exactly the same as in Example 2.3. When this procedure is followed, the node and secondary transformer voltages are
0.4 V
0.4 V
0.5 V
0.6 V
0.8 V
0.9 V
ECpE Department

## Slide 47: Thank You!
ECpE Department

## Slide 48
Load Duration Curve
Fig.7 Transformer diversified demand curve
A “load duration curve” can be developed for the transformer serving the four customers. Sorting in a descending order, the kW demand of the transformer develops the load duration curve shown in Fig.7.
The load duration curve plots the 15 min kW demand versus the percent of time the transformer operates at or above the specific kW demand. For example, the load duration curve shows the transformer operates with a 15 min kW demand of 12 kW or greater 22% of the time. This curve can be used to determine whether or not a transformer needs to be replaced due to an overloading condition.
ECpE Department