## Slide 1: Power Flow Calculation in Distribution Systems
EE 653 Power distribution system modeling, optimization and simulation
GRA: Qianzhi Zhang
Advisor: Dr. Zhaoyu Wang
Department of Electrical and Computer Engineering
Iowa State University

## Slide 2: Outline
Conventional power flow calculations in transmission systems
  Gauss-Seidel method
  Newton-Raphson method
Features of electrical distribution networks
  Ill-conditioned Jacobian matrix in Newton-Raphson method
Power flow calculations in distribution systems
  Forward/Backward sweep method
    Kirchhoff’s formulation
      BIBC & BCBV matrices
    Dist-flow formulation
      Linearized Dist-flow formulation
      Extension to three-phase systems
  Modified Newton-Raphson method

## Slide 3: Power flow calculation
Power flow analysis of power system is used to determine the steady state solution for a given set of bus loading condition.
Parameters
  Network topology
  Line conductance and susceptance ,
Variables
  Bus voltage magnitudes and bus phase angles ,
  Line active and reactive power flow ,

## Slide 4: Power flow calculation
Usually, two of the four variables are known for each bus:
  PQ bus (load) at which and are fixed; iteration solves for V and .
  PV bus (generator) at which P and V are fixed; iteration solves for and .
  Slack bus at which the V and are fixed; iteration solves for P and Q.

## Slide 5: Conventional power flow calculation in transmission systems
Gauss-Seidel method
  It needs to rewrite the equations in an implicit form:
  It starts with initial guess:
  Then we update the solution using the following form:
  It repeats the procedure until converged
It needs to put the equation in the correct form:
The update rule for each bus voltage:

## Slide 6: Conventional power flow calculation in transmission systems
Newton-Raphson method
  is the vector of and for all the buses, except for the slack bus.
  Active and reactive power balance equation:
where
J
Compared to Gauss-Seidel method, Newton-Raphson method has a faster convergence rate, but each iteration takes much longer time. Also, Newton-Raphson is more complicated to code.

## Slide 7: How to accelerate?
Decoupled Newton-Raphson method
  Approximation of the Jacobian matrix is used to decouple the real and reaction power equations.
J
Accelerated (convergence) Gauss-Seidel method
  Previously, it calculates each value as:
  To accelerate convergence, the above equation can be rewritten as:
  Acceleration parameter :
  Larger value of may result in faster convergence
Assume , thus

## Slide 8: Disadvantages of Gauss-Seidel and Newton-Raphson
Traditional Gauss-Seidel method and Newton-Raphson method need the calculation of the Y matrix and Jacobian matrix.
When solving large power systems, the most difficult computation task is inverting the Y matrix and Jacobian matrix:
Inverting a full matrix needs an order of operation, meaning the amount of computation increases with the cube of the size .
This amount of computation can be decreased substantially by recognizing both Y matrix and Jacobian matrix are sparse matrices.
Using sparse matrix methods results in a computational order of about .

## Slide 9: Features of electrical distribution networks
Because of the following special features in distribution network, the Y matrix and Jacobian matrix ceases to be diagonally dominant and convergence problems arise in power flow solutions that rely on its inverse [1].
Radial or near radial structure
High R/X rations
Un-transposed lines
Multi-phase, unbalanced, grounded or ungrounded operation
Multi-phase, multi-mode control distribution equipment
Unbalanced distributed load
Extremely large number of branches/nodes
Thus, traditional Gauss-Seidel method and Newton-Raphson method have lost popularity due to their poor convergence in distribution system studies.
[1] C. S. Cheng and D. Shirmohammadi, "A three-phase power flow method for real-time distribution system analysis," in IEEE Transactions on Power Systems, vol. 10, no. 2, pp. 671-679, May 1995.

## Slide 10: Convergence of Newton’s method for distribution systems
Condition number defines the condition of a matrix with respect to the computing problem. and are maximum and minimum eigenvalues of matrix .
A very high value of the condition number of matrix indicates that:
  The system is ill-conditioned, the computed values are very sensitive to small changes in input values.
  The matrix is invertible.
[2] S. C. Tripathy and G. S. S. S. K. Purge Prasad, "Load flow solution for ill-conditioned power systems by quadratically convergent Newton-like method," in IEE Proceedings C - Generation, Transmission and Distribution, vol. 127, no. 5, pp. 273-280, September 1980.
Tab.1 Maximum and Minimum Eigenvalues and Condition Number [2]

## Slide 11: Forward/Backward Sweep-based Algorithm
Methods developed for the solution of ill-conditioned radial distribution systems may be divided into two categories [3]:
  Forward and/or backward sweep
    Kirchhoff’s formulation
      BIBC & BCBV
    Quadratic equation-based algorithm
      Dist-Flow
  Modification of existing methods
    Modified N-R method
Forward/backward sweep-based power flow algorithm generally takes advantage of the radial network topology and consists of forward and backward sweep processes.
  The forward sweep is mainly the node voltage calculation from the sending end to the far end of the lines.
  The backward sweep is primarily the branch current or power summation from the far end to the sending end of the lines.
[3] U. Eminoglu & M. H. Hocaoglu, “Distribution Systems Forward/ Backward Sweep-based Power Flow Algorithms: A Review and Comparison Study’, in Electric Power Components and Systems, 37:1, 91-110, 2008

## Slide 12: Forward/Backward Sweep-based Algorithm
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.
Fig.3 Linear Ladder network [4]
Fig.1 shows a linear ladder network [4].
For the ladder network, it is assumed that all of the line impedances and load impedances are known along with the voltage (VS) at the source.
The solution for this network is to perform the “forward” sweep by calculating the voltage at node 5 (V5) under a no-load condition.
With no load currents there are no line currents, so the computed voltage at node 5 will equal that of the specified voltage at the source.
The “backward” sweep commences by computing the load current at node 5.
The load current I5 is

## Slide 13: Forward/Backward Sweep-based Algorithm
For this “end node” case, the line current I45 is equal to the load current I5. The “backward” sweep continues by applying Kirchhoff's voltage law (KVL) to calculate the voltage at node 4:
The load current I4 can be determined and then Kirchhoff's current law (KCL) applied to determine the line current I34:
Fig.3 Linear Ladder network [4]
KVL is applied to determine the node voltage V3. The backward sweep continues until a voltage (V1) has been computed at the source.
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.
=
…

## Slide 14: Forward/Backward Sweep-based Algorithm
The computed voltage V1 is compared to the specified voltage VS. There will be a difference between these two voltages. The ratio of the specified voltage to the compute voltage can be determined as
Since the network is linear, all of the line and load currents and node voltages in the network can be multiplied by the ratio for the final solution to the network.
Fig.3 Linear Ladder network [4]
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 15: Forward/Backward Sweep-based Algorithm
The linear network of Fig.3 is modified to a nonlinear network by replacing all of the constant load impedances by constant complex power loads as shown in Fig.4.
As with the linear network, the “forward” sweep computes the voltage at node 5 assuming no load. As before, the node 5 (end node) voltage will equal that of the specified source voltage. In general, the load current at each node is computed by
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.
Fig. 4 Nonlinear ladder network [4]

## Slide 16: Forward/Backward Sweep-based Algorithm
The “backward” sweep will determine a computed source voltage V1.
  As in the linear case, this first “iteration” will produce a voltage that is not equal to the specified source voltage VS. Because the network is nonlinear, multiplying currents and voltages by the ratio of the specified voltage to the computed voltage will not give the solution.
  The most direct modification using the ladder network theory is to perform a “forward” sweep. The forward sweep commences by using the specified source voltage and the line currents from the previous “backward” sweep. KVL is used to compute the voltage at node 2 by
Fig. 4 Nonlinear ladder network [4]
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 17: Forward/Backward Sweep-based Algorithm
This procedure is repeated for each line segment until a “new” voltage is determined at node 5.
  Using the “new” voltage at node 5, a second backward sweep is started that will lead to a “new” computed voltage at the source.
  The procedure shown earlier works but, in general, will require more time to converge. A modified version is to perform the “forward” sweep calculating all of the node voltages using the line currents from the previous “backward” sweep.
  The new “backward” sweep will use the node voltages from the previous “forward” sweep to compute the new load and line currents.
  In general, this modification will require more iterations but less time to converge. In this modified version of the ladder technique, convergence is determined by computing the ratio of difference between the voltages at the n − 1 and n iterations and the nominal line-to-neutral voltage. Convergence is achieved when all of the phase voltages at all nodes satisfy
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 18
A single-phase lateral is shown in Fig.5. The line impedance is
The impedance of the line segment 1–2 is
The impedance of the line segment 2–3 is
Fig.5 Single-phase lateral [4]
Example
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.
Use the modified ladder method to compute the load voltage.

## Slide 19
The loads are
The source voltage at node 1 is 7200 V.
Set initial conditions:
The first forward sweep:
Example
Fig.5 Single-phase lateral [4]
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 20
The first backward sweep:
The current flowing in the line segment 2–3 is
The load current at node 2 is
The second forward sweep:
The current in line segment 1–2 is
7
7
Example
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 21
At this point, the second backward sweep is used to compute the new line currents. Then it is followed by the third forward sweep.
After four iterations, the voltages have converged to an error of 0.000017 with the final voltages and currents of
[]7
[]7
[]3
[]1
Example
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 22
Forward/Backward Sweep-based Algorithm
Fig.6 Standard feeder series component model [4]
With reference to Fig.6, the forward and backward sweep equations are
Forward sweep:
Backward sweep:
It was also shown that for the grounded wye–delta transformer bank, the backward sweep equation is
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 23
Forward/Backward Sweep-based Algorithm
In Fig. 7, nodes 4, 10, 5, and 7 are referred to as “junction nodes.”
  In the forward sweep, the voltages at all nodes down the lines from the junction nodes must be computed.
  In the backward sweeps, the currents at the junction nodes must be summed before proceeding toward the source.
  In developing a program to apply the modified ladder method, it is necessary for the ordering of the lines and nodes to be such that all node voltages in the forward sweep are computed and all currents in the backward sweep are computed.
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.
Fig.7 Typical distribution feeder [4]

## Slide 24
Forward/Backward Sweep-based Algorithm
Fig.8 Simple modified ladder flowchart [4]
A simple flowchart of the Forward/Backward sweep-based algorithm is shown in Fig.8.
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.

## Slide 25: BIBC matrix and BCBV matrix
There are two matrices can be used to improve computational efficiency, which takes advantages of the topological characteristics of distribution systems and solves the distribution load flow [5]:
Bus Injection to Bus Current (BIBC) matrix: relationship between the bus current injections and branch currents
Branch current to Bus Voltage (BCBV) matrix: relationship between the branch currents and bus voltages
The reason why the BIBC and BCBV are applied:
In conventional forward/backward sweep method, the bus voltages and line currents are calculated segments by segments (with topological characteristics) in each iteration.
While by using the BIBC and BCBV, the two matrices are calculated only once and they have already included all topological information. BIBC/BCBV will not be updated in each iteration. Only voltage drop and branch currents will be updated.
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 26
++++
+
BIBC matrix and BCBV matrix
Fig.9 Equivalent Current Injection based Model of Distribution Network [5]
B is branch current
I is bus current injection
Relationship between the bus current injections and branch currents
The constant BIBC matrix is an upper triangular matrix and contains values of 0 and 1 only.
By using the KCL
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 27
BIBC matrix and BCBV matrix
To build BIBC matrix:
Step.1 For a distribution system with m-branch section and n-bus, the dimension of the BIBC matrix is .
Step.2 If a line section is located between bus i and bus j, copy the column of the i-th bus of the BIBC matrix to the column of the j-th bus and fill a +1 to the position of the k-th row and the j-th bus column
Step.3 Repeat Step.2 until all line sections are included in the BIBC matrix
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 28
BIBC matrix and BCBV matrix
Fig.10 Equivalent Current Injection based Model of Distribution Network [5]
V is bus voltage
Z is line impedance
Relationship between branch currents and bus voltages
[
The constant BIBC matrix is a lower triangular matrix and contains values of 0 and line impedance only.
By using the KVL
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 29
BIBC matrix and BCBV matrix
To build BCBV matrix:
Step.1 For a distribution system with m-branch section and n-bus, the dimension of the BCBV matrix is .
Step.2 If a line section is located between bus i and bus j, copy the column of the i-th bus of the BCBV matrix to the column of the j-th bus and fill the line impedance to the position of the j-th row and the k-th bus column.
Step.3 Repeat Step.2 until all line sections are included in the BCBV matrix.
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 30
Three-phase BCBV matrix
The algorithm can easily be expanded to a multiphase line section or bus.
For example, if the line section between bus i and bus j is a three-phase line section, the corresponding branch current will be a vector and the in the BIBC matrix will be a identity matrix.
Similarly, if the line section between bus i and bus j is a three-phase line section, the in the BCBV matrix is a impedance matrix as follows.
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.
Fig.11 Three-phase line section model [5]

## Slide 31
=
Distribution Load Flow (DLF) matrix is a multiplication matrix of BCBV and BIBC matrices.
[
BIBC matrix and BCBV matrix
The solution for distribution load flow can be updated and obtained iteratively as follows:
The voltage drop on each branch is computed using the DLF and load currents.
The node voltages are computed by using the source bus voltage and voltage drops.
Combine two steps into one
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 32: BIBC matrix and BCBV matrix
Step.1 Input the radial system topology data
Step.2 Form the BIBC matrix
Step.3 Form the BCBV matrix
Step.4 Calculate DLF matrix and set iteration k=0
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 33: BIBC matrix and BCBV matrix
Step.4 Calculate DLF matrix and set iteration k=0
Step.5 Update voltage and iteration k=k+1
Step.6 If tolerance, go to next step; else, go back to Step. 5
Step.7 Calculate line flows and power losses using final voltage
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 34
BIBC matrix and BCBV matrix
Some distribution feeders serve high-density load areas and contain loops. The proposed method introduced before can be extended for “weakly-meshed” distribution feeders.
Modification for BIBC matrix:
Fig.12 Simple distribution system with one loop [5]
Taking the new branch current into account, the current injections of bus 5 and bus 6 will be:
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 35
BIBC matrix and BCBV matrix
Modification for BCBV matrix:
Considering the loop shown in Fig. 12, KVL for this loop can be written as:
The new BCBV matrix is:
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.
Fig.12 Simple distribution system with one loop [5]

## Slide 36
BIBC matrix and BCBV matrix
Modification for solution techniques:
=
The modified algorithm for weakly meshed networks can be expressed as
Except for some modifications needed to be done for the BIBC, BCBV, and DLF matrices, the proposed solution techniques require no modification.
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 37: BIBC matrix and BCBV matrix
The proposed three-phase load flow algorithm was implemented on an 8-bus distribution system. Two methods are used for tests and the convergence tolerance is set at 0.001.
Method 1: The Gauss implicit Z-matrix method
Method 2: The proposed algorithm with BIBC and BCBV
Fig.13 A 8-bus radial distribution system [5]
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 38: BIBC matrix and BCBV matrix
The final voltage solutions of method 1 and method 2 are shown in Tab.2.
From Tab.2, the final converged voltage solutions of method 2 are very close to the solution of method 1.
It means that the accuracy of the proposed method is almost the same as the commonly used Gauss implicit -matrix method.
Tab. 2 Final Converged Voltage Solutions [5]
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 39: BIBC matrix and BCBV matrix
Tab.4 lists the number of iterations and the normalized execution time for both methods. It can be seen that method 2 is more efficient, especially when the network size increases,
It is because the time-consuming processes such as LU factorization and forward/backward substitution of Y-bus matrix are not necessary for method 2.
Tab. 3 Test Feeder [5]
Tab. 4 Number of iteration and Normalized Execution Time [5]
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.

## Slide 40: Node voltage calculations (quadratic equation)
The quadratic equation relates the voltage magnitude at the receiving end to the branch power and the voltage at the sending end.
Let us consider a distribution line model as below, the real and reactive power at the receiving end can be written as
+=1
(R+X) ( )
Node voltages are calculated by solving this quadratic equation
=
[3] U. Eminoglu & M. H. Hocaoglu, “Distribution Systems Forward/ Backward Sweep-based Power Flow Algorithms: A Review and Comparison Study’, in Electric Power Components and Systems, 37:1, 91-110, 2008
Fig.14A two-bus distribution network [3]

## Slide 41: Dist-Flow method (single phase)
Fig.15 Dist-Flow Demonstration [6]
: Power consumptions at Bus j+1
: Power generations at Bus j+1
: Complex impedance of the line between Bus j to Bus j+1
: Active and reactive power losses of the line between Bus j to Bus j+1
Active () and Reactive () Branch Power Flow from Bus j to Bus j+1:
2
Nodal Voltage () on Bus j+1:
[6] Q. Zhang, K. Dehghanpour and Z. Wang, "Distributed CVR in Unbalanced Distribution Systems With PV Penetration," in IEEE Transactions on Smart Grid, vol. 10, no. 5, pp. 5308-5319, Sept. 2019.

## Slide 42: Dist-Flow method (single phase)
Forward nodal voltage calculation:
2
Backward branch power flow and branch power loss calculation:
The calculation is ended when certain values (for example, bus voltages or the system’s total active and reactive power loss mismatches) are lower than a specified error value.

## Slide 43: Linearized Dist-Flow method (single phase)
The branch power flow and voltage constraints in Dist-Flow method have power loss terms () that make the problem nonlinear.
There are several methods to linearize the nonlinear power loss terms:
(1) Neglect the nonlinear terms
The linearization is based on the fact that the nonlinear terms are much smaller than the linear terms. So that the nonlinear terms are neglected for the sake of developing efficient solution algorithms.
However, it is noted that such linearization neglects an accurate calculation of power loss.
2
2

## Slide 44: Fully Linearized Dist-Flow method (single phase)
(2) Piecewise linear formulation (more accurate)
The quadratic calculation of branch active power losses () and reactive power losses () can be linearized through piecewise linear formulation.
Fig.16 Piecewise Linear Formulation [7]
Linear equation slopes
[7] C. Zhang, Y. Xu, Z. Dong and J. Ravishankar, "Three-Stage Robust Inverter-Based Voltage/Var Control for Distribution Networks With High-Level PV," in IEEE Transactions on Smart Grid, vol. 10, no. 1, pp. 782-793, Jan. 2019.

## Slide 45
Linear calculation for the complex power loss:
Piecewise power flow variable can vary only within its corresponding interval:
Fully Linearized Dist-Flow method (single phase)
0
0
0
0
Based on the piecewise linear formulation, the fully linearized Dist-Flow with power loss is developed as:
[7] C. Zhang, Y. Xu, Z. Dong and J. Ravishankar, "Three-Stage Robust Inverter-Based Voltage/Var Control for Distribution Networks With High-Level PV," in IEEE Transactions on Smart Grid, vol. 10, no. 1, pp. 782-793, Jan. 2019.

## Slide 46: Extension to unbalanced three-phase systems
Formulations are developed by L. Gan and S. Low at Caltech (Patent number: US20150346753A1) [8]:
Up to this point, it has only considered the single phase; however, distribution networks are inherently three-phase unbalanced.
Also, the coupling between phases for the system voltages requires additional approximations to simplify the unbalanced case.
[8] Gan, Lingwen, and Steven H. Low. "Systems and Methods for Convex Relaxations and Linear Approximations for Optimal Power Flow in Multiphase Radial Networks." U.S. Patent Application No. 14/724,757.

## Slide 47: Extension to unbalanced three-phase systems
In single-phase distribution system, it has
Where , , , ,
and denote the element-wise division multiplication, respectively.
Unlike the per-phase equivalent case, multiplying by the complex conjugate of both side of the three-phase formulation will not remove the dependence on .
This is due to the fact that there is a coupling between the phase at bus i that arises from the cross-products of the three-phase equations for the phase voltage and line current.
[9] Anmar Arif, “Distribution system outage management after extreme weather events”, PhD Dissertation, Iowa State University, 2019.
Extend to three-phase system, it has

## Slide 48: Extension to unbalanced three-phase systems
To address this problem, it has observed that the voltage magnitude between the phases are similar, i.e., , and that the phase unbalances on each bus are not very severe, so it assumes that the voltages are nearly balanced. Thus, it can approximate the phase different at bus i as:
Where represents the relative phase unbalance, which is sufficiently small. Therefore, the nearly balanced voltages are
[9] Anmar Arif, “Distribution system outage management after extreme weather events”, PhD Dissertation, Iowa State University, 2019.

## Slide 49: Extension to unbalanced three-phase systems
It can update the voltage magnitude in Dist-Flow method for the unbalanced case with
where
[9] Anmar Arif, “Distribution system outage management after extreme weather events”, PhD Dissertation, Iowa State University, 2019.
is Phase shift matrix

## Slide 50: Extension to unbalanced three-phase systems
Apply above equations to Dist-Flow formulation to for the extension to unbalanced three-phase systems.
[9] Anmar Arif, “Distribution system outage management after extreme weather events”, PhD Dissertation, Iowa State University, 2019.
=real()
=imag()

## Slide 51
Validation
Fig.17 IEEE 123-bus system: actual vs simulated results [9]
In [9], the validation of this unbalanced approximation method VS OpenDSS simulated results.
[9] Anmar Arif, “Distribution system outage management after extreme weather events”, PhD Dissertation, Iowa State University, 2019.

## Slide 52: Power flow in OpenDSS
However, OpenDSS manual [10] says that:
[10] “Reference guide: The OpenDSS”, [online]: https://www.epri.com/#/pages/sa/opendss?lang=en

## Slide 53: Modified Newton-Raphson method
[11] F. Zhang and C. S. Cheng, “A Modified Newton Method for Radial Distribution System Power Flow Analysis," in IEEE Transactions on Power System, vol. 12, no. 1, pp. 882-887, Feb 1997.
In [11], A modified Newton method for radial distribution system is derived in which the Jacobian matrix is in form, where is a constant upper triangular matrix depending only on system topology and is a block diagonal matrix. With this formulation, the conventional steps of forming the Jacobian matrix are replaced by back/forward sweeps on radial feeders with equivalent impedances.
In conventional Newton-Raphson method, the power flow problem is to solve
where

## Slide 54: Modified Newton-Raphson method
[11] F. Zhang and C. S. Cheng, “A Modified Newton Method for Radial Distribution System Power Flow Analysis," in IEEE Transactions on Power System, vol. 12, no. 1, pp. 882-887, Feb 1997.
Assumption 1: small voltage difference between two adjacent nodes (typical distribution lines are short and line flows are not high).
Assumption 2: no shunt branches (all the shunt branches can be converted to node power injections using initial and updated node voltages).
Therefore, the Jacobian matrix can be approximated as:
The matrices H, N, J and L all have the same properties (symmetry, sparsity pattern) as the Nodal Admittance Matrix.

## Slide 55: Modified Newton-Raphson method
[11] F. Zhang and C. S. Cheng, “A Modified Newton Method for Radial Distribution System Power Flow Analysis," in IEEE Transactions on Power System, vol. 12, no. 1, pp. 882-887, Feb 1997.
Hence, the matrices H, N, J and L can be formed as:
where and are diagonal matrices with diagonal entries to be and , respectively. Therefore, the conventional Newton Raphson can be rewritten as:
is an upper triangular matrix with all diagonal entries to be 1 and all non-zero off-diagonal entries to be -1.

## Slide 56: Modified Newton-Raphson method
[11] F. Zhang and C. S. Cheng, “A Modified Newton Method for Radial Distribution System Power Flow Analysis," in IEEE Transactions on Power System, vol. 12, no. 1, pp. 882-887, Feb 1997.
By now it has shown that the Jacobian matrix can be formed as the product of three square matrices. It can be solved by back/forward sweeps as well. It defines:
Therefore, the formulations in Newton-Raphson method can be modified:
=
=
When solving , the diagonal matrix can be inverted for each line. The diagonal in is denoted as the equivalent line impedance:
=j

## Slide 57: Modified Newton-Raphson method
[11] F. Zhang and C. S. Cheng, “A Modified Newton Method for Radial Distribution System Power Flow Analysis," in IEEE Transactions on Power System, vol. 12, no. 1, pp. 882-887, Feb 1997.
=
Backward sweep
Forward sweep
Fig.18 Flowchart of the modified Newton-Raphson method [11]

## Slide 58: References
[1] C. S. Cheng and D. Shirmohammadi, "A three-phase power flow method for real-time distribution system analysis," in IEEE Transactions on Power Systems, vol. 10, no. 2, pp. 671-679, May 1995.
[2] S. C. Tripathy and G. S. S. S. K. Purge Prasad, "Load flow solution for ill-conditioned power systems by quadratically convergent Newton-like method," in IEE Proceedings C - Generation, Transmission and Distribution, vol. 127, no. 5, pp. 273-280, September 1980.
[3] U. Eminoglu & M. H. Hocaoglu, “Distribution systems forward/ backward sweep-based power flow algorithms: a review and Comparison Study’, in Electric Power Components and Systems, 37:1, 91-110, 2008
[4] Kersting, William H. Distribution system modeling and analysis 4th edition. CRC press, 2017.
[5] Jen-Hao Teng, "A direct approach for distribution system load flow solutions," in IEEE Transactions on Power Delivery, vol. 18, no. 3, pp. 882-887, July 2003.
[6] Q. Zhang, K. Dehghanpour and Z. Wang, "Distributed CVR in unbalanced distribution systems with PV penetration," in IEEE Transactions on Smart Grid, vol. 10, no. 5, pp. 5308-5319, Sept. 2019.
[7] C. Zhang, Y. Xu, Z. Dong and J. Ravishankar, "Three-stage robust inverter-based voltage/var control for distribution networks with high-level PV," in IEEE Transactions on Smart Grid, vol. 10, no. 1, pp. 782-793, Jan. 2019.
[8] Gan, Lingwen, and Steven H. Low. "Systems and methods for convex relaxations and linear approximations for optimal power flow in multiphase radial networks." U.S. Patent Application No. 14/724,757.
[9] Anmar Arif, “Distribution system outage management after extreme weather events”, PhD Dissertation, Iowa State University, 2019.
[10] “Reference guide: The OpenDSS”, [online]: https://www.epri.com/#/pages/sa/opendss?lang=en
[11] F. Zhang and C. S. Cheng, “A modified newton method for radial distribution system power flow analysis," in IEEE Transactions on Power System, vol. 12, no. 1, pp. 882-887, Feb 1997.

## Slide 59: Thank you!