## Slide 1: OpenDSS – Modeling A Transformer
Dr. Zhaoyu Wang 1113 Coover Hall, Ames, IA wzy@iastate.edu
ECpE Department

## Slide 2: Modeling A Transformer in OpenDSS
ECpE Department
Single-phase Transformer
Three-phase Delta-Grounded Wye Step-down Transformer
Three-phase Delta-Grounded Wye Step-up Transformer
Three-phase Ungrounded Wye-Delta Step-down Transformer
Three-phase Ungrounded Wye-Delta Step-up Transformer
Three-phase Grounded Wye-Delta Step-down Transformer
Three-phase Grounded Wye-Grounded Wye Transformer
Three-phase Delta-Delta Transformer

## Slide 3: Modeling A Transformer in OpenDSS
ECpE Department
Single-phase Transformer
, where,

## Slide 4: Modeling A Transformer in OpenDSS
ECpE Department
Single-phase Transformer
Step 1: Compute the nodal admittance matrix on a one turn or one voltage base.
, where, ,
, where,
Also, , i.e.,
What is ?

## Slide 5: Modeling A Transformer in OpenDSS
ECpE Department
Single-phase Transformer
Step 2: Consider winding turns ratio.
, where, ,
, where,

## Slide 6: Modeling A Transformer in OpenDSS
ECpE Department
Single-phase Transformer
Step 2: Consider winding turns ratio.
. How to obtain ?

## Slide 7: Modeling A Transformer in OpenDSS
ECpE Department
Single-phase Transformer
Step 3: Consider winding connections.
. How to obtain ?
, where,.
, where,

## Slide 8: Modeling A Transformer in OpenDSS
ECpE Department
Single-phase Transformer
An example:
// Define a single-phase transformer.
New Transformer.xfmr phases=1 windings=2 xhl=5
~ wdg=1 bus=n kV=66.39 kva=50 %r=2.5
~ wdg=2 bus=m kV=4.16 kva=50 %r=2.5
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
Computing using Matlab:
, ,
Calculate =
0.000113 | -0.00011 | -0.00011 | 0.000113 | -0.00181 | 0.00181 | 0.00181 | -0.00181
-0.00011 | 0.000113 | 0.000113 | -0.00011 | 0.00181 | -0.00181 | -0.00181 | 0.00181
-0.00181 | 0.00181 | 0.00181 | -0.00181 | 0.028892 | -0.02889 | -0.02889 | 0.028892
0.00181 | -0.00181 | -0.00181 | 0.00181 | -0.02889 | 0.028892 | 0.028892 | -0.02889
Exported from OpenDSS:
G
B

## Slide 9: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Grounded Wye Step-down Transformer
Dyn1
Dyn1
HV winding Connection
LV winding Connection
Neutral Connection
Phase displacement of LV winding with reference to the HV winding
Note that
The HV side always comes before the LV side, regardless of which is the primary winding.
HV winding is taken as a reference.
Phase rotation is always counterclockwise.
1 = 30°, 2 = 60°, 3 = 90°, 6 = 180° and 12 = 0° or 360°.
https://en.wikipedia.org/wiki/Vector_group

## Slide 10: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 11: Modeling A Transformer in OpenDSS
ECpE Department
, where, , ,
, where, ,
1
2
3
Step 1: Compute the nodal admittance matrix on a one turn or one voltage base.
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 12: Modeling A Transformer in OpenDSS
ECpE Department
What is ?
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 13: Modeling A Transformer in OpenDSS
ECpE Department
, where ,
1
Step 2: Consider winding turns ratio.
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 14: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Note: For a delta-connected winding, ; for a Y-connected winding,
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 15: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 16: Modeling A Transformer in OpenDSS
ECpE Department
1
, where,.
Step 3: Consider winding connections
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 17: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 18: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Delta-Grounded Wye Step-down Transformer

## Slide 19: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Grounded Wye Step-down Transformer
An example:
// Define a three-phase transformer.
New Transformer.xfmr phases=3 windings=2 xhl=5
~ wdg=1 bus=K.1.2.3 conn=delta kV=115 kva=500 %r=1
~ wdg=2 bus=M.1.2.3.0 conn=wye kV=4.16 kva=500 %r=1
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
,
Winding connection
Computing using Matlab:

## Slide 20: Modeling A Transformer in OpenDSS
ECpE Department
Calculate =
Exported from OpenDSS:
G
B
Three-phase Delta-Grounded Wye Step-down Transformer
0.000174 | -0.00043 | -8.69E-05 | 0.000217 | -8.69E-05 | 0.000217 | -0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0
-8.69E-05 | 0.000217 | 0.000174 | -0.00043 | -8.69E-05 | 0.000217 | 0 | 0 | -0.00416 | 0.010404 | 0.004162 | -0.0104
-8.69E-05 | 0.000217 | -8.69E-05 | 0.000217 | 0.000174 | -0.00043 | 0.004162 | -0.0104 | 0 | 0 | -0.00416 | 0.010404
-0.00416 | 0.010404 | 0 | 0 | 0.004162 | -0.0104 | 0.199258 | -0.49814 | 0 | 0 | 0 | 0
0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0 | 0 | 0 | 0.199258 | -0.49814 | 0 | 0
0 | 0 | 0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0 | 0 | 0 | 0.199258 | -0.49814
1
2
3
4
5
6
1 2 3 4 5 6

## Slide 21: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Grounded Wye Step-up Transformer
As the IEC60076-1 standard has stated, the notation is HV-LV in sequence. Therefore, this step-up transformer with a delta-connected primary, and star-connected secondary, is not written as ‘dY1’, but ‘Yd1’. The 1 indicates the LV winding lags the HV by 30 degrees.
Note that
The HV side always comes before the LV side, regardless of which is the primary winding.
HV winding is taken as a reference.
Phase rotation is always counterclockwise.
1 = 30°, 2 = 60°, 3 = 90°, 6 = 180° and 12 = 0° or 360°.
https://en.wikipedia.org/wiki/Vector_group
YNd1

## Slide 22: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Grounded Wye Step-up Transformer

## Slide 23: Modeling A Transformer in OpenDSS
ECpE Department
Note:
Compared to the 3-phase delta-grounded wye step-down transformer, the equation, , still applies to a 3-phase delta-grounded wye step-up transformer. The only difference exists in the formation of matrix due to a different connection of delta winding, and the values of and . Specifically, according to the figure on the left, we have
Three-phase Delta-Grounded Wye Step-up Transformer

## Slide 24: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Grounded Wye Step-up Transformer
An example:
// Define a three-phase transformer.
New Transformer.xfmr phases=3 windings=2 xhl=5
~ wdg=1 bus=K.1.2.3 conn=delta kV=4.16 kva=500 %r=1
~ wdg=2 bus=M.1.2.3.0 conn=wye kV=115 kva=500 %r=1
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
,
Winding connection
Computing using Matlab:

## Slide 25: Modeling A Transformer in OpenDSS
ECpE Department
Calculate =
Exported from OpenDSS:
G
B
Three-phase Delta-Grounded Wye Step-up Transformer
0.132839 | -0.3321 | -0.06642 | 0.166048 | -0.06642 | 0.166048 | -0.00416 | 0.010404 | 0 | 0 | 0.004162 | -0.0104
-0.06642 | 0.166048 | 0.132839 | -0.3321 | -0.06642 | 0.166048 | 0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0
-0.06642 | 0.166048 | -0.06642 | 0.166048 | 0.132839 | -0.3321 | 0 | 0 | 0.004162 | -0.0104 | -0.00416 | 0.010404
-0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0 | 0.000261 | -0.00065 | 0 | 0 | 0 | 0
0 | 0 | -0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0 | 0.000261 | -0.00065 | 0 | 0
0.004162 | -0.0104 | 0 | 0 | -0.00416 | 0.010404 | 0 | 0 | 0 | 0 | 0.000261 | -0.00065
1
2
3
4
5
6
1 2 3 4 5 6

## Slide 26: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Ungrounded Wye-Delta Step-down Transformer
The HV side always comes before the LV side, regardless of which is the primary winding.
HV winding is taken as a reference.
Phase rotation is always counterclockwise.
1 = 30°, 2 = 60°, 3 = 90°, 6 = 180° and 12 = 0° or 360°.
YNd1

## Slide 27: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 28: Modeling A Transformer in OpenDSS
ECpE Department
, where, , ,
, where, ,
1
2
3
Step 1: Compute the nodal admittance matrix on a one turn or one voltage base.
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 29: Modeling A Transformer in OpenDSS
ECpE Department
What is ?
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 30: Modeling A Transformer in OpenDSS
ECpE Department
, where ,
1
Step 2: Consider winding turns ratio.
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 31: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 32: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 33: Modeling A Transformer in OpenDSS
ECpE Department
+
1
, where,.
Step 3: Consider winding connections
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 34: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 35: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Ungrounded Wye-Delta Step-down Transformer

## Slide 36: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Ungrounded Wye-Delta Step-down Transformer
An example:
// Define a three-phase transformer.
New Transformer.xfmr phases=3 windings=2 xhl=5
~ wdg=1 bus=K.1.2.3.4 conn=wye kV=115 kva=500 %r=1
~ wdg=2 bus=M.1.2.3 conn=delta kV=4.16 kva=500 %r=1
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
,
Winding connection
Computing using Matlab:

## Slide 37: Modeling A Transformer in OpenDSS
ECpE Department
Calculate =
Exported from OpenDSS:
G
B
0.000261 | -0.00065 | 0 | 0 | 0 | 0 | -0.00026 | 0.000652 | -0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0 | 0 | 0
0 | 0 | 0.000261 | -0.00065 | 0 | 0 | -0.00026 | 0.000652 | 0 | 0 | -0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0
0 | 0 | 0 | 0 | 0.000261 | -0.00065 | -0.00026 | 0.000652 | 0.004162 | -0.0104 | 0 | 0 | -0.00416 | 0.010404 | 0 | 0
-0.00026 | 0.000652 | -0.00026 | 0.000652 | -0.00026 | 0.000652 | 0.000782 | -0.00196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-0.00416 | 0.010404 | 0 | 0 | 0.004162 | -0.0104 | 0 | 0 | 0.132839 | -0.3321 | -0.06642 | 0.166048 | -0.06642 | 0.166048 | 0 | 0
0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0 | 0 | 0 | -0.06642 | 0.166048 | 0.132839 | -0.3321 | -0.06642 | 0.166048 | 0 | 0
0 | 0 | 0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0 | -0.06642 | 0.166048 | -0.06642 | 0.166048 | 0.132839 | -0.3321 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One row and one column of zeros are added to the delta-connected winding to make sure that the primary and second windings have the same size of admittance matrix.
Three-phase Ungrounded Wye-Delta Step-down Transformer
1
2
3
4
5
6
7
0
1 2 3 4 5 6 7 0

## Slide 38: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Ungrounded Wye-Delta Step-up Transformer
The HV side always comes before the LV side, regardless of which is the primary winding.
HV winding is taken as a reference.
Phase rotation is always counterclockwise.
1 = 30°, 2 = 60°, 3 = 90°, 6 = 180° and 12 = 0° or 360°.
Dyn1

## Slide 39: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Ungrounded Wye-Delta Step-up Transformer

## Slide 40: Modeling A Transformer in OpenDSS
ECpE Department
Note:
Compared to the 3-phase ungrounded wye-delta step-down transformer, the equation, , also applies to a 3-phase ungrounded wye-delta step-up transformer. The only difference exists in the formation of matrix due to a different connection of delta winding, and the values of and . Specifically, according to the figure on the left, we have
    +
Three-phase Ungrounded Wye-Delta Step-up Transformer

## Slide 41: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Ungrounded Wye-Delta Step-up Transformer
An example:
// Define a three-phase transformer.
New Transformer.xfmr phases=3 windings=2 xhl=5
~ wdg=1 bus=K.1.2.3.4 conn=wye kV=4.16 kva=500 %r=1
~ wdg=2 bus=M.1.2.3 conn=delta kV=115 kva=500 %r=1
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
,
Winding connection
Computing using Matlab:

## Slide 42: Modeling A Transformer in OpenDSS
0.199258 | -0.49814 | 0 | 0 | 0 | 0 | -0.19926 | 0.498145 | -0.00416 | 0.010404 | 0 | 0 | 0.004162 | -0.0104 | 0 | 0
0 | 0 | 0.199258 | -0.49814 | 0 | 0 | -0.19926 | 0.498145 | 0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.199258 | -0.49814 | -0.19926 | 0.498145 | 0 | 0 | 0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0
-0.19926 | 0.498145 | -0.19926 | 0.498145 | -0.19926 | 0.498145 | 0.597773 | -1.49443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0 | 0 | 0 | 0.000174 | -0.00043 | -8.69E-05 | 0.000217 | -8.69E-05 | 0.000217 | 0 | 0
0 | 0 | -0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0 | -8.69E-05 | 0.000217 | 0.000174 | -0.00043 | -8.69E-05 | 0.000217 | 0 | 0
0.004162 | -0.0104 | 0 | 0 | -0.00416 | 0.010404 | 0 | 0 | -8.69E-05 | 0.000217 | -8.69E-05 | 0.000217 | 0.000174 | -0.00043 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECpE Department
Calculate =
Exported from OpenDSS:
G
B
One row and one column of zeros are added to the delta-connected winding to make sure that the primary and second windings have the same size of admittance matrix.
Three-phase Ungrounded Wye-Delta Step-up Transformer
1
2
3
4
5
6
7
0
1 2 3 4 5 6 7 0

## Slide 43: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Grounded Wye-Delta Step-down Transformer
The HV side always comes before the LV side, regardless of which is the primary winding.
HV winding is taken as a reference.
Phase rotation is always counterclockwise.
1 = 30°, 2 = 60°, 3 = 90°, 6 = 180° and 12 = 0° or 360°.
YNd1

## Slide 44: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 45: Modeling A Transformer in OpenDSS
ECpE Department
, where, , ,
, where, ,
1
2
3
Step 1: Compute the nodal admittance matrix on a one turn or one voltage base.
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 46: Modeling A Transformer in OpenDSS
ECpE Department
What is ?
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 47: Modeling A Transformer in OpenDSS
ECpE Department
, where ,
1
Step 2: Consider winding turns ratio.
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 48: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 49: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 50: Modeling A Transformer in OpenDSS
ECpE Department
1
, where,.
Step 3: Consider winding connections
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 51: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 52: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Grounded Wye-Delta Step-down Transformer

## Slide 53: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Grounded Wye-Delta Step-down Transformer
An example:
// Define a three-phase transformer.
New Transformer.xfmr phases=3 windings=2 xhl=5
~ wdg=1 bus=K.1.2.3.0 conn=wye kV=115 kva=500 %r=1
~ wdg=2 bus=M.1.2.3 conn=delta kV=4.16 kva=500 %r=1
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
,
Winding connection
Computing using Matlab:

## Slide 54: Modeling A Transformer in OpenDSS
ECpE Department
Calculate =
Exported from OpenDSS:
G
B
Three-phase Grounded Wye-Delta Step-down Transformer
0.000261 | -0.00065 | 0 | 0 | 0 | 0 | -0.00416 | 0.010404 | 0.004162 | -0.0104 | 0 | 0
0 | 0 | 0.000261 | -0.00065 | 0 | 0 | 0 | 0 | -0.00416 | 0.010404 | 0.004162 | -0.0104
0 | 0 | 0 | 0 | 0.000261 | -0.00065 | 0.004162 | -0.0104 | 0 | 0 | -0.00416 | 0.010404
-0.00416 | 0.010404 | 0 | 0 | 0.004162 | -0.0104 | 0.132839 | -0.3321 | -0.06642 | 0.166048 | -0.06642 | 0.166048
0.004162 | -0.0104 | -0.00416 | 0.010404 | 0 | 0 | -0.06642 | 0.166048 | 0.132839 | -0.3321 | -0.06642 | 0.166048
0 | 0 | 0.004162 | -0.0104 | -0.00416 | 0.010404 | -0.06642 | 0.166048 | -0.06642 | 0.166048 | 0.132839 | -0.3321
1
2
3
4
5
6
1 2 3 4 5 6

## Slide 55: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Grounded Wye-Grounded Wye Transformer
The HV side always comes before the LV side, regardless of which is the primary winding.
HV winding is taken as a reference.
Phase rotation is always counterclockwise.
1 = 30°, 2 = 60°, 3 = 90°, 6 = 180° and 12 = 0° or 360°.
YNyn0

## Slide 56: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 57: Modeling A Transformer in OpenDSS
ECpE Department
, where, , ,
, where, ,
1
2
3
Step 1: Compute the nodal admittance matrix on a one turn or one voltage base.
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 58: Modeling A Transformer in OpenDSS
ECpE Department
What is ?
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 59: Modeling A Transformer in OpenDSS
ECpE Department
, where ,
1
Step 2: Consider winding turns ratio.
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 60: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 61: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 62: Modeling A Transformer in OpenDSS
ECpE Department
1
, where,.
Step 3: Consider winding connections
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 63: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 64: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Grounded Wye-Grounded Wye Transformer

## Slide 65: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Grounded Wye-Grounded Wye Transformer
An example:
// Define a three-phase transformer.
New Transformer.xfmr phases=3 windings=2 xhl=5
~ wdg=1 bus=K.1.2.3.0 conn=wye kV=115 kva=500 %r=1
~ wdg=2 bus=M.1.2.3.0 conn=wye kV=4.16 kva=500 %r=1
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
Winding connection
Computing using Matlab:

## Slide 66: Modeling A Transformer in OpenDSS
ECpE Department
Calculate =
Exported from OpenDSS:
G
B
Three-phase Grounded Wye-Grounded Wye Transformer
0.000261 | -0.00065 | 0 | 0 | 0 | 0 | -0.00721 | 0.01802 | 0 | 0 | 0 | 0
0 | 0 | 0.000261 | -0.00065 | 0 | 0 | 0 | 0 | -0.00721 | 0.01802 | 0 | 0
0 | 0 | 0 | 0 | 0.000261 | -0.00065 | 0 | 0 | 0 | 0 | -0.00721 | 0.01802
-0.00721 | 0.01802 | 0 | 0 | 0 | 0 | 0.199258 | -0.49814 | 0 | 0 | 0 | 0
0 | 0 | -0.00721 | 0.01802 | 0 | 0 | 0 | 0 | 0.199258 | -0.49814 | 0 | 0
0 | 0 | 0 | 0 | -0.00721 | 0.01802 | 0 | 0 | 0 | 0 | 0.199258 | -0.49814
1
2
3
4
5
6
1 2 3 4 5 6

## Slide 67: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Delta Transformer
The HV side always comes before the LV side, regardless of which is the primary winding.
HV winding is taken as a reference.
Phase rotation is always counterclockwise.
1 = 30°, 2 = 60°, 3 = 90°, 6 = 180° and 12 = 0° or 360°.
Dd0

## Slide 68: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Delta Transformer

## Slide 69: Modeling A Transformer in OpenDSS
ECpE Department
, where, , ,
, where, ,
1
2
3
Step 1: Compute the nodal admittance matrix on a one turn or one voltage base.
Three-phase Delta-Delta Transformer

## Slide 70: Modeling A Transformer in OpenDSS
ECpE Department
What is ?
Three-phase Delta-Delta Transformer

## Slide 71: Modeling A Transformer in OpenDSS
ECpE Department
, where ,
1
Step 2: Consider winding turns ratio.
Three-phase Delta-Delta Transformer

## Slide 72: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Delta-Delta Transformer

## Slide 73: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Delta-Delta Transformer

## Slide 74: Modeling A Transformer in OpenDSS
ECpE Department
1
, where,.
Step 3: Consider winding connections
Three-phase Delta-Delta Transformer

## Slide 75: Modeling A Transformer in OpenDSS
ECpE Department
2
, where,
Three-phase Delta-Delta Transformer

## Slide 76: Modeling A Transformer in OpenDSS
ECpE Department
. How to obtain ?
Three-phase Delta-Delta Transformer

## Slide 77: Modeling A Transformer in OpenDSS
ECpE Department
Three-phase Delta-Delta Transformer
An example:
// Define a three-phase transformer.
New Transformer.xfmr phases=3 windings=2 xhl=5
~ wdg=1 bus=K.1.2.3 conn=delta kV=115 kva=500 %r=1
~ wdg=2 bus=M.1.2.3 conn=delta kV=4.16 kva=500 %r=1
Transformer name
Number of phases
Number of windings
Percent reactance high-to-low
Specify which winding will be edited
Rated voltage
Base kVA rating
Percent resistance
,
Winding connection
Computing using Matlab:

## Slide 78: Modeling A Transformer in OpenDSS
ECpE Department
Calculate =
Exported from OpenDSS:
G
B
0.000174 | -0.00043 | -8.69E-05 | 0.000217 | -8.69E-05 | 0.000217 | -0.00481 | 0.012013 | 0.002403 | -0.00601 | 0.002403 | -0.00601
-8.69E-05 | 0.000217 | 0.000174 | -0.00043 | -8.69E-05 | 0.000217 | 0.002403 | -0.00601 | -0.00481 | 0.012013 | 0.002403 | -0.00601
-8.69E-05 | 0.000217 | -8.69E-05 | 0.000217 | 0.000174 | -0.00043 | 0.002403 | -0.00601 | 0.002403 | -0.00601 | -0.00481 | 0.012013
-0.00481 | 0.012013 | 0.002403 | -0.00601 | 0.002403 | -0.00601 | 0.132839 | -0.3321 | -0.06642 | 0.166048 | -0.06642 | 0.166048
0.002403 | -0.00601 | -0.00481 | 0.012013 | 0.002403 | -0.00601 | -0.06642 | 0.166048 | 0.132839 | -0.3321 | -0.06642 | 0.166048
0.002403 | -0.00601 | 0.002403 | -0.00601 | -0.00481 | 0.012013 | -0.06642 | 0.166048 | -0.06642 | 0.166048 | 0.132839 | -0.3321
Three-phase Delta-Delta Transformer
1
2
3
4
5
6
1 2 3 4 5 6

## Slide 79
ECpE Department
Thank you!