## Slide 1: OpenDSS - Three Typical Cases
Dr. Zhaoyu Wang 1113 Coover Hall, Ames, IA wzy@iastate.edu
ECpE Department

## Slide 2: Contents
ECpE Department
Static Snapshot Case
Time-series Static Case
Fault and Dynamic Case

## Slide 3: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Circuit
1 voltage source
13 buses
2 transformers
1 voltage regulator
1 switch
10 lines
8 spot loads
1 capacitor bank
1 1-phase capacitor
1 bus coordinate file

## Slide 4: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Given Parameters
Spot Load Data:
Capacitor Data:
 | kVA | kV-high | kV-low | R - % | X - %
Substation: | 5,000 | 115 - D | 4.16 Gr. Y | 1 | 8
XFM -1 | 500 | 4.16 – Gr.W | 0.48 – Gr.W | 1.1 | 2
Transformer Data:
Regulator ID: | 1 | 2 | 3
Connection: | 1-Ph,LG | 1-Ph,LG | 1-Ph,LG
Monitoring Phase: | A | B | C
Bandwidth: | 2.0 volts | 2.0 volts | 2.0 volts
PT Ratio: | 20 | 20 | 20
Primary CT Rating: | 700 | 700 | 700
Compensator Settings: | Ph-A | Ph-B | Ph-C
R - Setting: | 3 | 3 | 3
X - Setting: | 9 | 9 | 9
Volltage Level: | 122 | 122 | 122
Regulator Data:
Bus | Load | Ph-1 | Ph-1 | Ph-2 | Ph-2 | Ph-3 | Ph-3
 | Model | kW | kVAr | kW | kVAr | kW | kVAr
634 | Y-PQ | 160 | 110 | 120 | 90 | 120 | 90
645 | Y-PQ | 0 | 0 | 170 | 125 | 0 | 0
646 | D-Z | 0 | 0 | 230 | 132 | 0 | 0
652 | Y-Z | 128 | 86 | 0 | 0 | 0 | 0
671 | D-PQ | 385 | 220 | 385 | 220 | 385 | 220
675 | Y-PQ | 485 | 190 | 68 | 60 | 290 | 212
692 | D-I | 0 | 0 | 0 | 0 | 170 | 151
611 | Y-I | 0 | 0 | 0 | 0 | 170 | 80
 | TOTAL | 1158 | 606 | 973 | 627 | 1135 | 753
Bus | Ph-A | Ph-B | Ph-C
 | kVAr | kVAr | kVAr
675 | 200 | 200 | 200
611 |  |  | 100
Total | 200 | 200 | 300

## Slide 5: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Given Parameters
Config. | Phasing | Phase | Neutral | Spacing
 |  | ACSR | ACSR | ID
601 | B A C N | 556,500 26/7 | 4/0 6/1 | 500
602 | C A B N | 4/0 6/1 | 4/0 6/1 | 500
603 | C B N | 1/0 | 1/0 | 505
604 | A C N | 1/0 | 1/0 | 505
605 | C N | 1/0 | 1/0 | 510
Overhead Line Configuration Data:
Config. | Phasing | Cable | Neutral | Space ID
606 | A B C N | 250,000 AA, CN | None | 515
607 | A N | 1/0 AA, TS | 1/0 Cu | 520
Underground Line Configuration Data:
Bus A | Bus B | Length(ft.) | Config. | Phasing
632 | 645 | 500 | 603 | B,C
632 | 633 | 500 | 602 | A,B,C
633 | 634 | 0 | XFM-1 | A,B,C
645 | 646 | 300 | 603 | B,C
RG60 | 632 | 2000 | 601 | A,B,C
684 | 652 | 800 | 607 | A
632 | 671 | 2000 | 601 | A,B,C
671 | 684 | 300 | 604 | A,C
671 | 680 | 1000 | 601 | A,B,C
671 | 692 | 0 | Switch | A,B,C
684 | 611 | 300 | 605 | C
692 | 675 | 500 | 606 | A,B,C
Line Segment Data:
Base kV. | pu | Phasing | Angle | MVAsc3 | MVAsc1
115 | 1.0001 | A B C N | 30 | 20,000 | 21,000
Source Data:

## Slide 6: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Given Parameters
Configuration 601:
Z (R +jX) in ohms per mile
0.3465 1.0179 0.1560 0.5017 0.1580 0.4236
0.3375 1.0478 0.1535 0.3849
0.3414 1.0348
Configuration 602:
Z (R +jX) in ohms per mile
0.7526 1.1814 0.1580 0.4236 0.1560 0.5017
0.7475 1.1983 0.1535 0.3849
0.7436 1.2112
Configuration 603:
Z (R +jX) in ohms per mile
0.0000 0.0000 0.0000 0.0000 0.0000 0.0000
1.3294 1.3471 0.2066 0.4591
1.3238 1.3569
Configuration 604:
Z (R +jX) in ohms per mile
1.3238 1.3569 0.0000 0.0000 0.2066 0.4591
0.0000 0.0000 0.0000 0.0000
1.3294 1.3471
Configuration 605:
Z (R +jX) in ohms per mile
0.0000 0.0000 0.0000 0.0000 0.0000 0.0000
0.0000 0.0000 0.0000 0.0000
1.3292 1.3475
Configuration 606:
Z (R +jX) in ohms per mile
0.7982 0.4463 0.3192 0.0328 0.2849 -0.0143
0.7891 0.4041 0.3192 0.0328
0.7982 0.4463
B in micro Siemens per mile
96.8897 0.0000 0.0000
96.8897 0.0000
96.8897
Configuration 607:
Z (R +jX) in ohms per mile
1.3425 0.5124 0.0000 0.0000 0.0000 0.0000
0.0000 0.0000 0.0000 0.0000
0.0000 0.0000
B in micro Siemens per mile
88.9912 0.0000 0.0000
0.0000 0.0000
0.0000

## Slide 7: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Vsource
Base kV. | pu | Phasing | Angle | MVAsc3 | MVAsc1
606 | 1.0001 | A B C N | 30 | 20,000 | 21,000
Source Data:
// define a new circuit
Clear
Set DefaultBaseFrequency=60
new circuit.IEEE13Nodeckt
~ basekv=115 pu=1.0001 phases=3 bus1=SourceBus
~ Angle=30
~ MVAsc3=20000 MVASC1=21000
OpenDSS Code:

## Slide 8: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Vsource
// define a new circuit
Clear
Set DefaultBaseFrequency=60
new circuit.IEEE13Nodeckt
~ basekv=115 pu=1.0001 phases=3 bus1=SourceBus
~ Angle=30
~ MVAsc3=20000 MVASC1=21000
OpenDSS Code:
Explanation:
// or !
“//” or “!” indicate that this statement is a comment line.
Clear
Clears all circuit element definitions from the DSS. This statement is recommended at the beginning of all Master files for defining DSS circuits.

## Slide 9: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Vsource
// define a new circuit
Clear
Set DefaultBaseFrequency=60
new circuit.IEEE13Nodeckt
~ basekv=115 pu=1.0001 phases=3 bus1=SourceBus
~ Angle=30
~ MVAsc3=20000 MVASC1=21000
OpenDSS Code:
Set DefaultBaseFrequency
It sets Default Base Frequency, in Hz. The default value when first installed is 60 Hz. {50|60}, Hz
Explanation:
New circuit.IEEE13Nodeckt
It creates a new circuit object named IEEE13Nodeckt.

## Slide 10: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Vsource
// define a new circuit
Clear
Set DefaultBaseFrequency=60
new circuit.IEEE13Nodeckt
~ basekv=115 pu=1.0001 phases=3 bus1=SourceBus
~ Angle=30
~ MVAsc3=20000 MVASC1=21000
OpenDSS Code:
~
It is a More Command. The More command continues editing the active object. The same as M or More.
Explanation:
basekv (Vsource)
Sets the nominal Line‐to‐line kV of Vsource.

## Slide 11: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Vsource
// define a new circuit
Clear
Set DefaultBaseFrequency=60
new circuit.IEEE13Nodeckt
~ basekv=115 pu=1.0001 phases=3 bus1=SourceBus
~ Angle=30
~ MVAsc3=20000 MVASC1=21000
OpenDSS Code:
Explanation:
pu
Actual per unit at which the source is operating. It is assumed balanced for all phases. In general, the voltage range is generally ±5% of the nominal voltage. That means the pu is in the range of 0.95~1.05.
phases
Number of phases. Default = 3.0. {1|2|3}.

## Slide 12: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Vsource
// define a new circuit
Clear
Set DefaultBaseFrequency=60
new circuit.IEEE13Nodeckt
~ basekv=115 pu=1.0001 phases=3 bus1=SourceBus
~ Angle=30
~ MVAsc3=20000 MVASC1=21000
OpenDSS Code:
Explanation:
bus1
Name of bus to which the source's first terminal is connected.
Angle
Base angle, in degrees, of the first phase.
MVAsc3
3‐phase short circuit MVA.

## Slide 13: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Vsource
// define a new circuit
Clear
Set DefaultBaseFrequency=60
new circuit.IEEE13Nodeckt
~ basekv=115 pu=1.0001 phases=3 bus1=SourceBus
~ Angle=30
~ MVAsc3=20000 MVASC1=21000
OpenDSS Code:
Explanation:
MVAsc1
1‐phase short circuit MVA.
* MVAsc3 and MVAsc1 are used for determining the positive- and zero-sequence impedances, i.e., Z1=R1+jX1 and Z0=R0+jX0. In general, they are obtained from system data. Default x1/r1 is 4.0 and Default x0/r0 is 3.0.

## Slide 14: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Transformer
// Substation transformer definitions
New Transformer.Sub Phases=3 Windings=2 XHL=8
~ wdg=1 bus=SourceBus conn=delta kv=115 kva=5000 %r=0.5
~ wdg=2 bus=650 conn=wye kv=4.16 kva=5000 %r=0.5
OpenDSS Code:
 | kVA | kV-high | kV-low | R - % | X - %
Substation: | 5,000 | 115 - D | 4.16 Gr. Y | 1 | 8
XFM -1 | 500 | 4.16 – Gr.W | 0.48 – Gr.W | 1.1 | 2
Transformer Data:

## Slide 15: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Transformer
// Substation transformer definitions
New Transformer.Sub Phases=3 Windings=2 XHL=8
~ wdg=1 bus=SourceBus conn=delta kv=115 kva=5000 %r=0.5
~ wdg=2 bus=650 conn=wye kv=4.16 kva=5000 %r=0.5
OpenDSS Code:
Explanation:
New Transformer.Sub
Defines a transformer object named Sub.
Phases
Number of phases. Default is 3. {1|3}
Windings
Number of windings. Default is 2. {2|3|4}

## Slide 16: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Transformer
// Substation transformer definitions
New Transformer.Sub Phases=3 Windings=2 XHL=8
~ wdg=1 bus=SourceBus conn=delta kv=115 kva=5000 %r=0.5
~ wdg=2 bus=650 conn=wye kv=4.16 kva=5000 %r=0.5
OpenDSS Code:
Explanation:
XHL (or X12)
Percent reactance high‐to‐low (winding1 to winding 2).
Wdg
It specifies an integer representing the winding which will become the active winding for subsequent data.
 | kVA | kV-high | kV-low | R - % | X - %
Substation: | 5,000 | 115 - D | 4.16 Gr. Y | 1 | 8

## Slide 17: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Transformer
// Substation transformer definitions
New Transformer.Sub Phases=3 Windings=2 XHL=8
~ wdg=1 bus=SourceBus conn=delta kv=115 kva=5000 %r=0.5
~ wdg=2 bus=650 conn=wye kv=4.16 kva=5000 %r=0.5
OpenDSS Code:
Explanation:
bus
It specifies the name of bus to which the winding is connected.
conn
It Specifies the connection of this winding. One of {wye | ln} for wye connected banks or {delta | ll} for delta (line‐line) connected banks. Default is wye.

## Slide 18: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Transformer
// Substation transformer definitions
New Transformer.Sub Phases=3 Windings=2 XHL=8
~ wdg=1 bus=SourceBus conn=delta kv=115 kva=5000 %r=0.5
~ wdg=2 bus=650 conn=wye kv=4.16 kva=5000 %r=0.5
OpenDSS Code:
Explanation:
kv
It specifies the rated voltage of this winding, in kV. For transformers designated 2‐ or 3‐phase, enter phase-to‐phase kV. For all other designations, enter actual winding kV rating. Default is 12.47 kV.
kva
It specifies the base kVA rating of this winding.

## Slide 19: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Transformer
// Substation transformer definitions
New Transformer.Sub Phases=3 Windings=2 XHL=8
~ wdg=1 bus=SourceBus conn=delta kv=115 kva=5000 %r=0.5
~ wdg=2 bus=650 conn=wye kv=4.16 kva=5000 %r=0.5
OpenDSS Code:
Explanation:
%r
It specifies the percent resistance of this winding on the rated kVA base. (It equals half of total for a 2-winding transformer).
* Transformer parameters are obtained from transformer nameplate.
 | kVA | kV-high | kV-low | R - % | X - %
Substation: | 5,000 | 115 - D | 4.16 Gr. Y | 1 | 8
*0.5

## Slide 20: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
Voltage Regulator Data:
Regulator ID: | 1 | 2 | 3
Connection: | 1-Ph,LG | 1-Ph,LG | 1-Ph,LG
Monitoring Phase: | A | B | C
Bandwidth: | 2.0 volts | 2.0 volts | 2.0 volts
PT Ratio: | 20 | 20 | 20
Primary CT Rating: | 700 | 700 | 700
Compensator Settings: | Ph-A | Ph-B | Ph-C
R - Setting: | 3 | 3 | 3
X - Setting: | 9 | 9 | 9
Volltage Level: | 122 | 122 | 122
// Voltage Regulator Definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
New Transformer.Reg2 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.2 RG60.2] kVs=[2.4 2.4]
new regcontrol.Reg2 transformer=Reg2 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
New Transformer.Reg3 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.3 RG60.3] kVs=[2.4 2.4]
new regcontrol.Reg3 transformer=Reg3 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9

## Slide 21: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
// Voltage regulator and control definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
Explanation:
Note that voltage regulator is defined using the class of transformer. Different with the transformer, additional RegControl Object should be defined for each regulator.
New Transformer.Reg1
Defines a regulator named Reg1.
phases
Specifies Number of phases.

## Slide 22: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
// Voltage regulator and control definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
Explanation:
bank
Specifies the name of the bank this regulator is part of.
XHL (or X12)
Specifies the percent reactance high‐to‐low (winding 1 to winding 2).

## Slide 23: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
// Voltage regulator and control definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
Explanation:
kVAs=[1666 1666]
Specifies an array of base kVA ratings for windings [1, 2]. The kVA rating of winding 1 is 1666kVA, the kVA rating of winding 2 is 1666 kVA.
* Note that compared with the aforementioned way of defining the properties of transformer windings, i.e., specifying the properties for each winding, individually, this is another way of defining the winding properties, i.e., using property arrays.

## Slide 24: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
// Voltage regulator and control definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
Explanation:
kVs=[2.4 2.4]
Specifies an array of kV ratings for windings [1,2]. The kV rating of winding 1 is 2.4 kV, the kV rating of winding 2 is 2.4 kV.
Buses=[650.1 RG60.1]
Specifies an array of the names of buses to which the windings [1, 2] are connected. Winding 1 is connected to Bus 650, winding 2 is connected to Bus RG60.

## Slide 25: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
// Voltage regulator and control definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
Explanation:
new regcontrol.Reg1
Defines a regulator control object named Reg1.
transformer
Specifies the name of transformer to which the RegControl is connected.
winding
Specifies the number of transformer winding that the RegControl is monitoring. 1 or 2, typically.

## Slide 26: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
// Voltage regulator and control definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
Explanation:
vreg
Specifies the voltage regulator setting, in volts, for the winding being controlled.
band
Specifies the bandwidth, in volts, for the controlled bus. Default is 3.0.
ptratio
Specifies the ratio of the PT that converts the controlled winding voltage to the regulator voltage. Default is 60. If the winding is Wye, the line-to-neutral voltage is used. Else, the line-to-line voltage is used.

## Slide 27: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model -- Regulator
OpenDSS Code:
// Voltage regulator and control definitions
New Transformer.Reg1 phases=1 bank=reg1 XHL=0.01 kVAs=[1666 1666]
~ Buses=[650.1 RG60.1] kVs=[2.4 2.4]
new regcontrol.Reg1 transformer=Reg1 winding=2 vreg=122 band=2 ptratio=20 ctprim=700 R=3 X=9
Explanation:
ctprim
Specifies the rating, in Amperes, of the primary CT rating for converting the line amps to control amps. The typical default secondary ampere rating is 0.2 Amps.
R
Specifies the R setting on the line drop compensator in the regulator, in VOLTS.
X
Specifies the X setting on the line drop compensator in the regulator, in VOLTS.

## Slide 28: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Line Configuration
OpenDSS Code:
Line Configuration Data:
// Linecode definitions
New Linecode.mtx606 nphases=3 Units=mi
~ Rmatrix=[0.7982 |0.3192 0.7891 |0.2849 0.3192 0.7982 ]
~ Xmatrix=[0.4463 |0.0328 0.4041 |-0.0143 0.0328 0.4463 ]
~ Cmatrix=[257.01 |0 257.01 |0 0 257.01 ]
~ units=mi
New linecode.mtx607 nphases=1 BaseFreq=60
~ rmatrix = (1.3425 )
~ xmatrix = (0.5124 )
~ cmatrix = [236.06]
~ units=mi
Configuration 606:
Z (R +jX) in ohms per mile
0.7982 0.4463 0.3192 0.0328 0.2849 -0.0143
0.7891 0.4041 0.3192 0.0328
0.7982 0.4463
B in micro Siemens per mile
96.8897 0.0000 0.0000
96.8897 0.0000
96.8897
Configuration 607:
Z (R +jX) in ohms per mile
1.3425 0.5124 0.0000 0.0000 0.0000 0.0000
0.0000 0.0000 0.0000 0.0000
0.0000 0.0000
B in micro Siemens per mile
88.9912 0.0000 0.0000
0.0000 0.0000
0.0000

## Slide 29: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Line configuration
OpenDSS Code:
// Linecode definitions
New Linecode.mtx606 nphases=3 BaseFreq=60
~ Rmatrix=[0.7982 |0.3192 0.7891 |0.2849 0.3192 0.7982 ]
~ Xmatrix=[0.4463 |0.0328 0.4041 |-0.0143 0.0328 0.4463 ]
~ Cmatrix=[257.01 |0 257.01 |0 0 257.01 ]
~ units=mi
Explanation:
New linecode.mtx606
Defines a linecode object named mtx606.
nphases
Specifies the number of phases. Default = 3.
BaseFreq
Specifies the Base Frequency at which the impedance values are specified. {50 | 60}, Hz, Default = 60.0 Hz.

## Slide 30: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Line configuration
OpenDSS Code:
// Linecode definitions
New Linecode.mtx606 nphases=3 BaseFreq=60
~ Rmatrix=[0.7982 |0.3192 0.7891 |0.2849 0.3192 0.7982 ]
~ Xmatrix=[0.4463 |0.0328 0.4041 |-0.0143 0.0328 0.4463 ]
~ Cmatrix=[257.01 |0 257.01 |0 0 257.01 ]
~ units=mi
Explanation:
Rmatrix
Defines the series resistance matrix, in ohms per unit length. The order of matrices expected is the number of phases. The matrices may be entered in lower triangle form or full matrix. The result is always symmetrical.
The "|" separates rows.
Xmatrix
Similar with Rmatrix, Xmatrix is a series reactance matrix, in ohms per unit length.

## Slide 31: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Line configuration
OpenDSS Code:
// Linecode definitions
New Linecode.mtx606 nphases=3 BaseFreq=60
~ Rmatrix=[0.7982 |0.3192 0.7891 |0.2849 0.3192 0.7982 ]
~ Xmatrix=[0.4463 |0.0328 0.4041 |-0.0143 0.0328 0.4463 ]
~ Cmatrix=[257.01 |0 257.01 |0 0 257.01 ]
~ units=mi
Explanation:
Cmatrix
Defines the shunt nodal capacitance matrix, in nanofarads per unit length. The order of matrices expected is the number of phases. The matrices may be entered in lower triangle form or full matrix. The result is always symmetrical.
The "|" separates rows.
Units
Specifies the length units of linecode. If not specified, it is assumed that the units correspond to the length being used in the Line models. {mi|kft|km|m|Ft|in|cm}.

## Slide 32: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Line
OpenDSS Code:
Line Segment Data:
// Line definitions
New Line.632645 Phases=2 Bus1=632.3.2 Bus2=645.3.2 LineCode=mtx603 Length=500 units=ft
New Line.632633 Phases=3 Bus1=632.1.2.3 Bus2=633.1.2.3 LineCode=mtx602 Length=500 units=ft
New Line.645646 Phases=2 Bus1=645.3.2 Bus2=646.3.2 LineCode=mtx603 Length=300 units=ft
New Line.RG60632 Phases=3 Bus1=RG60.1.2.3 Bus2=632.1.2.3 LineCode=mtx601 Length=2000 units=ft
New Line.684652 Phases=1 Bus1=684.1 Bus2=652.1 LineCode=mtx607 Length=800 units=ft
New Line.632671 Phases=3 Bus1=632.1.2.3 Bus2=671.1.2.3 LineCode=mtx601 Length=2000 units=ft
New Line.671684 Phases=2 Bus1=671.1.3 Bus2=684.1.3 LineCode=mtx604 Length=300 units=ft
New Line.671680 Phases=3 Bus1=671.1.2.3 Bus2=680.1.2.3 LineCode=mtx601 Length=1000 units=ft
New Line.684611 Phases=1 Bus1=684.3 Bus2=611.3 LineCode=mtx605 Length=300 units=ft
New Line.692675 Phases=3 Bus1=692.1.2.3 Bus2=675.1.2.3 LineCode=mtx606 Length=500 units=ft
Node A | Node B | Length(ft.) | Config. | Phasing
632 | 645 | 500 | 603 | B,C
632 | 633 | 500 | 602 | A,B,C
645 | 646 | 300 | 603 | B,C
RG60 | 632 | 2000 | 601 | A,B,C
684 | 652 | 800 | 607 | A
632 | 671 | 2000 | 601 | A,B,C
671 | 684 | 300 | 604 | A,C
671 | 680 | 1000 | 601 | A,B,C
684 | 611 | 300 | 605 | C
692 | 675 | 500 | 606 | A,B,C

## Slide 33: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Line
OpenDSS Code:
// Line definitions
New Line.632645 Phases=2 Bus1=632.3.2 Bus2=645.3.2 LineCode=mtx603 Length=500 units=ft
Explanation:
New Line.650632
Defines a line object named 650632.
Phases
Specifies the number of phases. Default = 3.
Bus1
Specifies the name of bus for terminal 1.
Bus2
Specifies the name of bus for terminal 2.
LineCode
Specifies the name of an existing LineCode object containing impedance definitions.

## Slide 34: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Line
OpenDSS Code:
// Line definitions
New Line.632645 Phases=2 Bus1=632.3.2 Bus2=645.3.2 LineCode=mtx603 Length=500 units=ft
Explanation:
Length
Specifies a length multiplier to be applied to the impedance data.
Units
Specifies the length Units = {none | mi | kft | km | m | Ft | in | cm}.

## Slide 35: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Load
OpenDSS Code:
// Load definitions
New Load.634a Bus1=634.1 Phases=1 Conn=Wye Model=1 kV=0.277 kW=160 kvar=110
New Load.634b Bus1=634.2 Phases=1 Conn=Wye Model=1 kV=0.277 kW=120 kvar=90
New Load.634c Bus1=634.3 Phases=1 Conn=Wye Model=1 kV=0.277 kW=120 kvar=90
New Load.645 Bus1=645.2 Phases=1 Conn=Wye Model=1 kV=2.4 kW=170 kvar=125
New Load.646 Bus1=646.2.3 Phases=1 Conn=Delta Model=2 kV=4.16 kW=230 kvar=132
New Load.652 Bus1=652.1 Phases=1 Conn=Wye Model=2 kV=2.4 kW=128 kvar=86
New Load.671 Bus1=671.1.2.3 Phases=3 Conn=Delta Model=1 kV=4.16 kW=1155 kvar=660
New Load.675a Bus1=675.1 Phases=1 Conn=Wye Model=1 kV=2.4 kW=485 kvar=190
New Load.675b Bus1=675.2 Phases=1 Conn=Wye Model=1 kV=2.4 kW=68 kvar=60
New Load.675c Bus1=675.3 Phases=1 Conn=Wye Model=1 kV=2.4 kW=290 kvar=212
New Load.692 Bus1=692.3.1 Phases=1 Conn=Delta Model=5 kV=4.16 kW=170 kvar=151
New Load.611 Bus1=611.3 Phases=1 Conn=Wye Model=5 kV=2.4 kW=170 kvar=80
Spot Load Data:
Node | Load | Ph-1 | Ph-1 | Ph-2 | Ph-2 | Ph-3 | Ph-3
 | Model | kW | kVAr | kW | kVAr | kW | kVAr
634 | Y-PQ | 160 | 110 | 120 | 90 | 120 | 90
645 | Y-PQ | 0 | 0 | 170 | 125 | 0 | 0
646 | D-Z | 0 | 0 | 230 | 132 | 0 | 0
652 | Y-Z | 128 | 86 | 0 | 0 | 0 | 0
671 | D-PQ | 385 | 220 | 385 | 220 | 385 | 220
675 | Y-PQ | 485 | 190 | 68 | 60 | 290 | 212
692 | D-I | 0 | 0 | 0 | 0 | 170 | 151
611 | Y-I | 0 | 0 | 0 | 0 | 170 | 80

## Slide 36: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Load
OpenDSS Code:
// Load definitions
New Load.634a Bus1=634.1 Phases=1 Conn=Wye Model=1 kV=0.277 kW=160 kvar=110
Explanation:
New Load.634a
Defines a load object named 634a.
Phases
Specifies the number of phases of this load.
Conn
{wye | y | LN} for Wye (Line‐Neutral) connection; {delta | LL} for Delta (Line‐Line) connection. Default = wye.
Bus1
Specifies the name of bus to which the load is connected.

## Slide 37: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Load
OpenDSS Code:
// Load definitions
New Load.634a Bus1=634.1 Phases=1 Conn=Wye Model=1 kV=0.277 kW=160 kvar=110
Explanation:
Model
An integer defining how the load will vary with voltage. The load models currently implemented are:
1: Constant P and constant Q (Default): Commonly used for power flow studies,
2: Constant Z (or constant impedance),
3: Constant P and quadratic Q (),
4: Exponential: and
5: Constant I (or constant current magnitude),
6: Constant P and fixed Q (at the nominal value)
7: Constant P and quadratic Q (i.e., fixed reactance),
8: ZIP
…

## Slide 38: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Load
OpenDSS Code:
// Load definitions
New Load.634a Bus1=634.1 Phases=1 Conn=Wye Model=1 kV=0.277 kW=160 kvar=110
Explanation:
Model
…
"Constant" power value (either P or Q) may be modified by loadshape multipliers. "Fixed" power values are always the same.
kV
Specifies the Base voltage for load. For 2‐ or 3‐phase loads, it is specified in phase‐to‐phase kV.
For all other loads, it is specified in the actual kV across the load branch. If the load is wye (star) connected, then specify phase‐to‐neutral (L‐N) kV. If the load is delta or phase‐to‐phase connected, specify the phase‐to‐phase (L‐L) kV.

## Slide 39: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Load
OpenDSS Code:
// Load definitions
New Load.634a Bus1=634.1 Phases=1 Conn=Wye Model=1 kV=0.277 kW=160 kvar=110
Explanation:
kW
Specifies the nominal active power, in kW, for the load. Total of all phases.
kVar
Specifies the nominal reactive power, in kVar, for the load. Total of all phases.
* If there is no specification, the kW and kVar are divided evenly in each phase. If the load is unbalanced, the load should be defined for each phase.

## Slide 40: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Capacitor
OpenDSS Code:
// Capacitor definitions
New Capacitor.Cap1 Bus1=675 phases=3 kVAR=600 kV=4.16
New Capacitor.Cap2 Bus1=611.3 phases=1 kVAR=100 kV=2.4
Capacitor Data:
Node | Ph-A | Ph-B | Ph-C
 | kVAr | kVAr | kVAr
675 | 200 | 200 | 200
611 |  |  | 100

## Slide 41: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Capacitor
OpenDSS Code:
// Capacitor definitions
New Capacitor.Cap1 Bus1=675 phases=3 kVAR=600 kV=4.16
New Capacitor.Cap2 Bus1=611.3 phases=1 kVAR=100 kV=2.4
Explanation:
New Capacitor.Cap1
Define a capacitor object named Cap1.
Bus1
Specifies the name of the first bus to which the capacitor is connected.
phases
Specifies the number of phases.
kVAR
Specifies the rated kvar at rated kV, total of all phases. Each phase is assumed equal.
kV
For 2- or 3-phase, enter line‐to‐line rated voltage. For 1-phase, enter line-to-ground rated voltage. (For Delta connection this is always line‐to‐line rated voltage).

## Slide 42: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Switch
OpenDSS Code:
// Switch definitions
New Line.671692 Phases=3 Bus1=671 Bus2=692 Switch=y r1=1e-4 r0=1e-4 x1=0.000 x0=0.000 c1=0.000 c0=0.000
Node A | Node B | Length(ft.) | Config. | Phasing
671 | 692 | 0 | Switch | A,B,C
Switch Data:

## Slide 43: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Switch
OpenDSS Code:
// Switch definitions
New Line.671692 Phases=3 Bus1=671 Bus2=692 Switch=y r1=1e-4 r0=1e-4 x1=0.000 x0=0.000 c1=0.000 c0=0.000
Explanation:
New Line.671692
Defines a line object named 671692.
Phases
Specifies the number of phases.
* In OpenDss, a switch object is defined as a special line object.
Bus1
Specifies the name of bus for terminal 1.
Bus2
Specifies the name of bus for terminal 2.
Switch
Specifies whether this line is a switch or not. {y/n | T/F}. Default= no/false.
y or T: Designates this line as a switch; n or F: Does not designate this line as a switch.

## Slide 44: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Switch
OpenDSS Code:
// Switch definitions
New Line.671692 Phases=3 Bus1=671 Bus2=692 Switch=y r1=1e-4 r0=1e-4 x1=0.000 x0=0.000 c1=0.000 c0=0.000
Explanation:
r1
Specifies the positive‐sequence resistance, in ohms per unit length.
r0
Specifies the zero‐sequence resistance, in ohms per unit length.
x1
Specifies the positive‐sequence reactance, in ohms per unit length.
x0
Specifies the zero‐sequence reactance, in ohms per unit length.
c1
Specifies the positive‐sequence capacitance, in nanofarads per unit length.
c0
Specifies the zero‐sequence capacitance, in nanofarads per unit length.

## Slide 45: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Solve
OpenDSS Code:
// Solve
Set Voltagebases=[115, 4.16, .48]
calcv
Set mode=snap
Set algorithm=normal
Solve
BusCoords IEEE13Node_BusXY.csv
Explanation:
Set Voltagebases
Defines the bus voltage bases for the defined circuit. You can enter an array of the legal voltage bases, in phase‐to‐phase voltages.
The voltage level can be selected from the following values: .208, .480, 12.47, 24.9, 34.5, 115.0, 230.0

## Slide 46: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Solve
OpenDSS Code:
Explanation:
calcv
Also called CalcVoltageBases.
Estimates the voltage base for each bus based on the array of voltage bases defined with a "Set Voltagebases=..." command. The voltage base for each bus is then set to the nearest voltage base specified in the voltage base array.
// Solve
Set Voltagebases=[115, 4.16, .48]
calcv
Set mode=snap
Set algorithm=normal
Solve
BusCoords IEEE13Node_BusXY.csv
Specifies the solution mode for the active circuit.
Snap = Solve a single snapshot power flow for the present conditions.
Set mode=snap

## Slide 47: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Solve
OpenDSS Code:
Explanation:
Solve
Solves the circuit. Default mode is snapshot.
Buscoords
Defines x,y coordinates for buses via reading coordinates from a CSV file.
It executes after the Solve command is executed, so that bus lists are defined.
Bus Name | X | Y
SourceBus | 200 | 400
650 | 200 | 350
RG60 | 200 | 300
646 | 0 | 250
645 | 100 | 250
632 | 200 | 250
633 | 350 | 250
634 | 400 | 250
611 | 0 | 100
684 | 100 | 100
671 | 200 | 100
692 | 250 | 100
675 | 400 | 100
652 | 100 | 0
680 | 200 | 0
// Solve
Set Voltagebases=[115, 4.16, .48]
calcv
Set mode=snap
Set algorithm=normal
Solve
BusCoords IEEE13Node_BusXY.csv
Set algorithm=normal
Specifies the solution algorithm type. {Normal | Newton}

## Slide 48: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Show
OpenDSS Code:
// Show
Show Voltages LN Nodes
Show Currents Elem
Show Powers kVA Elem
Show Losses
Show Taps
Explanation:
Show Voltages LN Nodes
Shows the line-to-ground voltages by node. (Report)
Show Currents Elem
Shows currents of circuit elements. (Report)
The Show command generally writes a text file report of the specified quantity for the most recent solution, and opens a viewer (the default Editor ‐‐ e.g., Notepad or some other editor) to display the file.

## Slide 49: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Show
OpenDSS Code:
// Show
Show Voltages LN Nodes
Show Currents Elem
Show Powers kVA Elem
Show Losses
Show Taps
Explanation:
Show Losses
Shows losses of power delivery elements. (Report)
Show Powers kVA Elem
Shows powers of circuit elements in kVA. (Report)
Show Taps
Shows the controlled transformer’s tap positions. (Report)

## Slide 50: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Visualization
OpenDSS Code:
// Visualization
Visualize what=currents element=Line.632633
Visualize what=voltages element=Line.632633
Explanation:
What=currents
Specifies that currents of circuit elements are visualized, in amps.
element=Line.632633
Specifies which element are visualized.
Shows the currents, voltages, or powers for selected element on a drawing in phasor quantities.

## Slide 51: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Plot
OpenDSS Code:
// Plot
Set markCapacitors=yes CapMarkersize=3
Set markRegulators=yes RegMarkersize=5
AddBusMarker Bus=632 code=34 color=Red size=3
Plot Circuit Power Max=2000 dots=y labels=n C1=Blue 1ph=3
Plot circuit Losses Max=0.02 dots=y labels=n subs=n C1=Blue
ClearBusMarkers
Explanation:
Set markCapacitors=yes
Marks Capacitor object locations with a symbol. {YES/TRUE | NO/FALSE} Default is NO.
Set CapMarkersize=3
Specifies the size of Capacitor marker on the plot. Default is 3.

## Slide 52: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Plot
OpenDSS Code:
// Plot
Set markCapacitors=yes CapMarkersize=3
Set markRegulators=yes RegMarkersize=5
AddBusMarker Bus=632 code=34 color=Red size=3
Plot Circuit Power Max=2000 dots=y labels=n C1=Blue 1ph=3
Plot circuit Losses Max=0.02 dots=y labels=n subs=n C1=Blue
ClearBusMarkers
Explanation:
Bus=632
Specifies the bus to which the marker is added.
AddBusMarker
Adds a marker to a bus in a circuit plot before issuing the Plot command.

## Slide 53: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Plot
OpenDSS Code:
// Plot
Set markCapacitors=yes CapMarkersize=3
Set markRegulators=yes RegMarkersize=5
AddBusMarker Bus=632 code=34 color=Red size=3
Plot Circuit Power Max=2000 dots=y labels=n C1=Blue 1ph=3
Plot circuit Losses Max=0.02 dots=y labels=n subs=n C1=Blue
ClearBusMarkers
Explanation:
Code=34
Specifies the Number code for bus marker on circuit plots. Marker codes are:

## Slide 54: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Plot
OpenDSS Code:
// Plot
Set markCapacitors=yes CapMarkersize=3
Set markRegulators=yes RegMarkersize=5
AddBusMarker Bus=632 code=34 color=Red size=3
Plot Circuit Power Max=2000 dots=y labels=n C1=Blue 1ph=3
Plot circuit Losses Max=0.02 dots=y labels=n subs=n C1=Blue
ClearBusMarkers
Explanation:
color=red
Specifies the color of the bus marker on circuit plots.
size=3
Specifies the size of the bus marker on circuit plots.
plot
Displays a variety of results in a variety of manners on graphs.

## Slide 55: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Plot
OpenDSS Code:
// Plot
Set markCapacitors=yes CapMarkersize=3
Set markRegulators=yes RegMarkersize=5
AddBusMarker Bus=632 code=34 color=Red size=3
Plot Circuit Power Max=2000 dots=y labels=n C1=Blue 1ph=3
Plot circuit Losses Max=0.02 dots=y labels=n subs=n C1=Blue
ClearBusMarkers
Explanation:
Circuit
Creates displays on which the thicknesses of LINE are varied according to: Power, Current, Voltage or Losses.
Max=2000
Specifies the value corresponding to max scale or line thickness on the circuit plots. Power and Losses in kW.
dots=y
Specifies whether to show buses as dots or not. {y | n}

## Slide 56: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Plot
OpenDSS Code:
// Plot
Set markCapacitors=yes CapMarkersize=3
Set markRegulators=yes RegMarkersize=5
AddBusMarker Bus=632 code=34 color=Red size=3
Plot Circuit Power Max=2000 dots=y labels=n C1=Blue 1ph=3
Plot circuit Losses Max=0.02 dots=y labels=n subs=n C1=Blue
ClearBusMarkers
Explanation:
labels=n
Specifies whether to show bus names or not. {y | n}
C1=Bule
Specifies the unicolor on circuit plots. Colors may be specified by their RGB color number or standard color names.
1ph=3
Specifies the Line style for drawing 1-phase lines. It is a number in the range of [1..7]. Default is 1 (solid). Use 3 for dotted; 2 for dashed.

## Slide 57: Case 1: IEEE 13 Bus Test Feeder
ECpE Department
Build OpenDSS Model – Plot
OpenDSS Code:
// Plot
Set markCapacitors=yes CapMarkersize=3
Set markRegulators=yes RegMarkersize=5
AddBusMarker Bus=632 code=34 color=Red size=3
Plot Circuit Power Max=2000 dots=y labels=n C1=Blue 1ph=3
Plot circuit Losses Max=0.02 dots=y labels=n subs=n C1=Blue
ClearBusMarkers
Explanation:
subs=n
Specifies whether to display a marker at each transformer declared to be a substation. At least one bus coordinate must be defined for the transformer. {Yes | No*}
ClearBusMarkers
Clears the present definitions of bus markers.

## Slide 58: Contents
ECpE Department
Static Snapshot Case
Time-series Static Case
Fault and Dynamic Case

## Slide 59: Case II: Time-series Power Flow
ECpE Department
Circuit
* Time range : 1 day, Time resolution: 1 second (86,400 snapshots)
1 capacitor with control
1 regulator with control
1 wind generator
4 monitors
Line 1
Line 2
Line 3
1 voltage source
1 substation transformer
3 line segments
2 time-series spot loads

## Slide 60: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Circuit, Vsource
clear
New object=circuit.ExampleCircuit
~ basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
OpenDSS Code:
Explanation:
Clear
Clears all circuit element definitions from the DSS. This statement is recommended at the beginning of all Master files for defining DSS circuits.
New object=circuit.ExampleCircuit
Defines a new circuit named ExampleCircuit.
~
More Command. The More command continues editing the active object. The same as M or More.

## Slide 61: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Circuit, Vsource
clear
New object=circuit.ExampleCircuit
~ basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
OpenDSS Code:
Explanation:
basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
There are two ways of setting property values of DSS circuit elements.
1. Simply specify the setting using complete element and property name, “=”, and a value. For example,
New Line.line1.R1=.05 X1=.12 R0=.1 X0=.4
2. Positional property rule. For example, we can use
New Line.line1.R1=.05 .12 .1 .4
to set the R1, X1, R0, X0 properties of Line.line1 in sequence, which is equivalent to the code using 1st way. In this case, the 2nd way is adopted.

## Slide 62: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Circuit, Vsource
clear
New object=circuit.ExampleCircuit
~ basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
OpenDSS Code:
Explanation:
basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
The above code equals: basekv=115 pu=1.00 Angle=0.0 Frequency=60.0 Phases=3 Mvasc3=20000 Mvasc1=21000 x1r1=4.0 x0r0=3.0
basekv: Specifies the voltage Base or rated Line‐to‐line kV of Vsource.
pu: Specifies the actual per unit at which the source is operating. It is assumed balanced for all phases.
Angle: Specifies the Base angle, in degrees, of the first phase.
Frequency: Specifies the frequency of the source.
…

## Slide 63: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Circuit, Vsource
clear
New object=circuit.ExampleCircuit
~ basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
OpenDSS Code:
Explanation:
basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
This above code equals: basekv=115 pu=1.00 Angle=0.0 Frequency=60.0 Phases=3 Mvasc3=20000 Mvasc1=21000 x1r1=4.0 x0r0=3.0
phases: Specifies the number of phases. Default = 3.0.
MVAsc3: Specifies the 3‐phase short circuit MVA.
MVAsc1: Specifies the1‐phase short circuit MVA.
x1r1: Specifies the ratio of X1/R1. Default = 4.0.
x0r0: Specifies the ratio of X0/R0. Default = 3.0.

## Slide 64: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Substation transformer
// Define Substation transformer
New transformer.subxfrm phases=3 windings=2 buses=(SourceBus subbus)
~ conns='delta wye' kvs=(115 12.47) kvas=(20000 20000) XHL=7
OpenDSS Code:
Explanation:
New transformer.subxfrm
Defines a transformer object named subxfrm.
phases
windings
Specifies the total number of windings. Default is 2.
Specifies the number of phases. Default is 3.

## Slide 65: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Substation transformer
// Define Substation transformer
New transformer.subxfrm phases=3 windings=2 buses=(SourceBus subbus)
~ conns='delta wye' kvs=(115 12.47) kvas=(20000 20000) XHL=7
OpenDSS Code:
Explanation:
bus1: Specifies the name of bus for terminal 1.
bus2: Specifies the name of bus for terminal 2.
conns='delta wye'
Specify that the connection of winding1 is ‘delta’, the connection of winding2 is ‘wye’.
buses=(SourceBus subbus)
The above command equals: bus1=SourceBus bus2=subbus

## Slide 66: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Substation transformer
// Define Substation transformer
New transformer.subxfrm phases=3 windings=2 buses=(SourceBus subbus)
~ conns='delta wye' kvs=(115 12.47) kvas=(20000 20000) XHL=7
OpenDSS Code:
Explanation:
kvs=(115 12.47)
Specify that the rated voltage of winding 1 is 115 kV. The rated voltage of winding 2 is 12.47kV.
kvas=(20000 20000)
Specify that the base kVA rating of winding1 is 20000 kVA. The base kVA rating of winding2 is 20000kVA.
XHL
Specify the percent reactance high‐to‐low (winding 1 to winding 2).

## Slide 67: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Linecode
// Define a linecode for the lines - unbalanced 336 MCM ACSR connection
New linecode.336matrix nphases=3
~ rmatrix=(0.0868455 | 0.0298305 0.0887966 | 0.0288883 0.0298305 0.0868455)
~ xmatrix=(0.2025449 | 0.0847210 0.1961452 | 0.0719161 0.0847210 0.2025449)
~ cmatrix=(2.74 | -0.70 2.96| -0.34 -0.71 2.74)
~ Normamps = 400 Emergamps=600
OpenDSS Code:
Explanation:
New linecode.336matrix
Defines a linecode object named 336matrix.
nphases
Specifies the number of phases. Default = 3.

## Slide 68: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Linecode
// Define a linecode for the lines - unbalanced 336 MCM ACSR connection
New linecode.336matrix nphases=3
~ rmatrix=(0.0868455 | 0.0298305 0.0887966 | 0.0288883 0.0298305 0.0868455)
~ xmatrix=(0.2025449 | 0.0847210 0.1961452 | 0.0719161 0.0847210 0.2025449)
~ cmatrix=(2.74 | -0.70 2.96| -0.34 -0.71 2.74)
~ Normamps = 400 Emergamps=600
OpenDSS Code:
Explanation:
rmatrix
Series resistance matrix, in ohms per unit length. The order of matrices expected is the number of phases. The matrices may be entered in lower triangle form or full matrix. The result is always symmetrical.
The "|" separates rows.
xmatrix
Series reactance matrix, in ohms per unit length. Similar with rmatrix.

## Slide 69: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Linecode
// Define a linecode for the lines - unbalanced 336 MCM ACSR connection
New linecode.336matrix nphases=3
~ rmatrix=(0.0868455 | 0.0298305 0.0887966 | 0.0288883 0.0298305 0.0868455)
~ xmatrix=(0.2025449 | 0.0847210 0.1961452 | 0.0719161 0.0847210 0.2025449)
~ cmatrix=(2.74 | -0.70 2.96| -0.34 -0.71 2.74)
~ Normamps = 400 Emergamps=600
OpenDSS Code:
Explanation:
cmatrix
Shunt nodal capacitance matrix, in nanofarads per unit length. The order of matrices expected is the number of phases. The matrices may be entered in lower triangle form or full matrix. The result is always symmetrical.
The "|" separates rows.

## Slide 70: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Linecode
// Define a linecode for the lines - unbalanced 336 MCM ACSR connection
New linecode.336matrix nphases=3
~ rmatrix=(0.0868455 | 0.0298305 0.0887966 | 0.0288883 0.0298305 0.0868455)
~ xmatrix=(0.2025449 | 0.0847210 0.1961452 | 0.0719161 0.0847210 0.2025449)
~ cmatrix=(2.74 | -0.70 2.96| -0.34 -0.71 2.74)
~ Normamps = 400 Emergamps=600
OpenDSS Code:
Explanation:
Normamps
Specifies the normal ampacity, in amperes.
Emergamps
Specifies the emergency ampacity, in amperes.

## Slide 71: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Line
// Define the lines
New line.line1 bus1=subbus bus2=loadbus1 linecode=336matrix length=10 units=kft
New line.line2 loadbus1 loadbus2 336matrix 10
New line.line3 Loadbus2 loadbus3 336matrix 20
OpenDSS Code:
Explanation:
New line.l1
Defines a line object named l1.
Bus1
Bus2
Specifies the name of bus for terminal 2.
Specifies the name of bus for terminal 1.

## Slide 72: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Line
// Define the lines
New line.line1 bus1=subbus bus2=loadbus1 linecode=336matrix length=10 units=kft
New line.line2 loadbus1 loadbus2 336matrix 10
New line.line3 Loadbus2 loadbus3 336matrix 20
OpenDSS Code:
Explanation:
LineCode
Specifies the name of an existing LineCode object containing impedance definitions.
Length
Specifies a length multiplier to be applied to the impedance data.
units
Specifies the length Units.
{none | mi | kft | km | m | Ft | in | cm }

## Slide 73: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Loadshape
// Define some load shapes for the loads and wind
New loadshape.day 8 3.0
~ mult=(.3 .36 .48 .62 .87 .95 .94 .60)
New loadshape.wind 2400 {1 24 /}
~ mult=(file=zavwind.csv) action=normalize
OpenDSS Code:
Explanation:
A Loadshape object is very important for all types of sequential power flow solutions. It consists of a series of multipliers, typically ranging from 0.0 to 1.0 which are applied to the base kW values of the load, to represent variation of the load over some time period.
New loadshape.day 8 3.0
Defines a loadshape object named day.
The above code equals: New loadshape.day Npts=8 Interval=3.0.

## Slide 74: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Loadshape
// Define some load shapes for the loads and wind
New loadshape.day 8 3.0
~ mult=(.3 .36 .48 .62 .87 .95 .94 .60)
New loadshape.wind 2400 {1 24 /}
~ mult=(file=zavwind.csv) action=normalize
OpenDSS Code:
Explanation:
New loadshape.day 8 3.0
New loadshape.day Npts=8 Interval=3.0.
Npts: Specifies the number of points to expect when defining the curve.
Interval: Specifies the time interval of the data, in Hr. Default=1.0. If the load shape has non‐uniformly spaced points, specify the interval as 0.0.
Note:
In defaults: the loadshape is constant during each 3-hr interval. 8*3=24 hrs.
For the loadshape named wind, 2400*1/24=100 hrs. Considering the simulation time range is 24 hours (specified later), the remaining 76 points are clipped.

## Slide 75: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Loadshape
// Define some load shapes for the loads and wind
New loadshape.day 8 3.0
~ mult=(.3 .36 .48 .62 .87 .95 .94 .60)
New loadshape.wind 2400 {1 24 /}
~ mult=(file=zavwind.csv) action=normalize
OpenDSS Code:
Explanation:
Mult
Specifies an array of multiplier values. It looks for Npts values. Omitted values are assumed to be zero, and extra values are ignored.
You may also use the syntax:
Mult=[file=myfile.txt],
Mult=[file=myfile.csv]
Mult=[dblfile=myfile.dbl],
Mult=[sngfile=myfile.sng]

## Slide 76: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Loadshape
// Define some load shapes for the loads and wind
New loadshape.day 8 3.0
~ mult=(.3 .36 .48 .62 .87 .95 .94 .60)
New loadshape.wind 2400 {1 24 /}
~ mult=(file=zavwind.csv) action=normalize
OpenDSS Code:
Explanation:
action
After defining the load curve data, setting action=normalize will modify the multipliers so that the peak is 1.0. The mean and std deviation are recomputed.

## Slide 77: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Load
// Define the loads
New load.load1 bus1=loadbus1 phases=3 kv=12.47 kw=1000.0 pf=0.88 model=1
~ class=1 duty=day
New load.load2 bus1=loadbus2 phases=3 kv=12.47 kw=500.0 pf=0.88 model=1
~ class=1 duty=day conn=delta
OpenDSS Code:
Explanation:
New Load.load1
Defines a load object named load1.
bus1
Specifies the name of bus to which the load is connected.
phases
Specifies the number of phases of this load.

## Slide 78: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Load
// Define the loads
New load.load1 bus1=loadbus1 phases=3 kv=12.47 kw=1000.0 pf=0.88 model=1
~ class=1 duty=day
New load.load2 bus1=loadbus2 phases=3 kv=12.47 kw=500.0 pf=0.88 model=1
~ class=1 duty=day conn=delta
OpenDSS Code:
Explanation:
kv
Specifies the Base voltage for load. For 2‐ or 3‐phase loads, it is specified in phase‐to‐phase kV.
For all other loads, it is specified in the actual kV across the load branch. If the load is wye (star) connected, then specify phase‐to‐neutral (L‐N) kV. If the load is delta or phase‐to‐phase connected, specify the phase‐to‐phase (L‐L) kV.
kw
Specifies the nominal active power, in kW, for the load. Total of all phases.

## Slide 79: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Load
// Define the loads
New load.load1 bus1=loadbus1 phases=3 kv=12.47 kw=1000.0 pf=0.88 model=1
~ class=1 duty=day
New load.load2 bus1=loadbus2 phases=3 kv=12.47 kw=500.0 pf=0.88 model=1
~ class=1 duty=day conn=delta
OpenDSS Code:
Explanation:
pf
Specifies the nominal power factor for load. Negative PF is leading. Specify either PF or kvar. If both are specified, the last one specified takes precedence.
Model
An integer defining how the load will vary with voltage. The load models currently implemented are:
1: Constant P and constant Q (Default): Commonly used for power flow studies,
…

## Slide 80: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Load
// Define the loads
New load.load1 bus1=loadbus1 phases=3 kv=12.47 kw=1000.0 pf=0.88 model=1
~ class=1 duty=day
New load.load2 bus1=loadbus2 phases=3 kv=12.47 kw=500.0 pf=0.88 model=1
~ class=1 duty=day conn=delta
OpenDSS Code:
Explanation:
Model
…
2: Constant Z (or constant impedance),
3: Constant P and quadratic Q (𝑄⁄𝑄0=(𝑉⁄𝑉0)^2),
4: Exponential: 𝑃⁄𝑃0=(𝑉⁄𝑉0)^𝐶𝑉𝑅𝑤𝑎𝑡𝑡𝑠 and 𝑄⁄𝑄0=(𝑉⁄𝑉0)^𝐶𝑉𝑅𝑣𝑎𝑟𝑠
5: Constant I (or constant current magnitude),
6: Constant P and fixed Q (at the nominal value)
7: Constant P and quadratic Q (i.e., fixed reactance),
…

## Slide 81: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Load
// Define the loads
New load.load1 bus1=loadbus1 phases=3 kv=12.47 kw=1000.0 pf=0.88 model=1
~ class=1 duty=day
New load.load2 bus1=loadbus2 phases=3 kv=12.47 kw=500.0 pf=0.88 model=1
~ class=1 duty=day conn=delta
OpenDSS Code:
Explanation:
Model
…
8: ZIP
"Constant" power value (either P or Q) may be modified by loadshape multipliers. "Fixed" power values are always the same.

## Slide 82: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Load
// Define the loads
New load.load1 bus1=loadbus1 phases=3 kv=12.47 kw=1000.0 pf=0.88 model=1
~ class=1 duty=day
New load.load2 bus1=loadbus2 phases=3 kv=12.47 kw=500.0 pf=0.88 model=1
~ class=1 duty=day conn=delta
OpenDSS Code:
Explanation:
class
An integer number segregating the load according to a particular class.
duty
Specifies the name of duty cycle load shape. Defaults to Daily load shape if not defined.
conn
Specifies the winding connection. {wye | y | LN} for Wye (Line‐Neutral) connection; {delta | LL} for Delta (Line‐Line) connection. Default = wye.

## Slide 83: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Capacitor
// Capacitor with control
New capacitor.Cap1 bus1=loadbus2 phases=3 kvar=600 kv=12.47
New capcontrol.Cap1Ctrl element=line.line3 terminal=1 capacitor=Cap1
~ type=current ctratio=1 ONsetting=60 OFFsetting=55 delay=2
OpenDSS Code:
Explanation:
New Capacitor.Cap1
Defines a capacitor object named Cap1.
Bus1
Specifies the name of the first bus to which the capacitor is connected.
phases
Specifies the number of phases.
kvar
Specifies the rated kvar at rated kV, total of all phases. Each phase is assumed equal.

## Slide 84: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Capacitor
// Capacitor with control
New capacitor.Cap1 bus1=loadbus2 phases=3 kvar=600 kv=12.47
New capcontrol.Cap1Ctrl element=line.line3 terminal=1 capacitor=Cap1
~ type=current ctratio=1 ONsetting=60 OFFsetting=55 delay=2
OpenDSS Code:
Explanation:
kv
Specifies the kV rating of capacitor. For Phases=2 or Phases=3, enter line‐to‐line (phase‐to‐phase) rated voltage. For all other numbers of phases, enter actual can rating. (For Delta connection this is always line‐to‐line rated voltage).
New capcontrol.Cap1Ctrl
Defines a capacitor control object named Cap1Ctrl.
* The capacitor control monitors the voltage and current at a terminal of a PDelement or a PCelement and sends switching messages to a Capacitor object.

## Slide 85: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Capacitor
// Capacitor with control
New capacitor.Cap1 bus1=loadbus2 phases=3 kvar=600 kv=12.47
New capcontrol.Cap1Ctrl element=line.line3 terminal=1 capacitor=Cap1
~ type=current ctratio=1 ONsetting=60 OFFsetting=55 delay=2
OpenDSS Code:
Explanation:
element
Specifies the full object name of the circuit element, typically a line or transformer, to which the capacitor control's PT and/or CT are connected. There is no default; must be specified.
terminal
Specifies the number of terminal of the circuit element to which the CapControl is connected. 1 or 2, typically. Default is 1.

## Slide 86: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Capacitor
// Capacitor with control
New capacitor.Cap1 bus1=loadbus2 phases=3 kvar=600 kv=12.47
New capcontrol.Cap1Ctrl element=line.line3 terminal=1 capacitor=Cap1
~ type=current ctratio=1 ONsetting=60 OFFsetting=55 delay=2
OpenDSS Code:
Explanation:
capacitor
Specifies the name of Capacitor which the CapControl controls. No Default; Must be specified.
type
Specifies the Control type. {Current | voltage | kvar | PF | time }.
ctratio
Specifies the ratio of the CT from line amps to control ampere setting for current and kvar control types.

## Slide 87: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Capacitor
// Capacitor with control
New capacitor.Cap1 bus1=loadbus2 phases=3 kvar=600 kv=12.47
New capcontrol.Cap1Ctrl element=line.line3 terminal=1 capacitor=Cap1
~ type=current ctratio=1 ONsetting=60 OFFsetting=55 delay=2
OpenDSS Code:
Explanation:
onsetting
Specifies the value at which the control arms to switch the capacitor ON. For different types of control, the value is calculated by:
Current: Line Amps / CTratio
Voltage: Line‐Neutral (or Line‐Line for delta) Volts / PTratio
kvar: Total kvar, all phases. This is directional.
PF: Power Factor, Total power in monitored terminal.
Time: Hrs from Midnight as a floating point number (decimal). 7:30am would be entered as 7.5.

## Slide 88: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Capacitor
// Capacitor with control
New capacitor.Cap1 bus1=loadbus2 phases=3 kvar=600 kv=12.47
New capcontrol.Cap1Ctrl element=line.line3 terminal=1 capacitor=Cap1
~ type=current ctratio=1 ONsetting=60 OFFsetting=55 delay=2
OpenDSS Code:
Explanation:
offsetting
Specifies the value at which the control arms to switch the capacitor OFF. For different types of control, the value is calculated by:
Current: Line Amps / CTratio
Voltage: Line‐Neutral (or Line‐Line for delta) Volts / PTratio
kvar: Total kvar, all phases. This is directional.
PF: Power Factor, Total power in monitored terminal.
Time: Hrs from Midnight as a floating point number (decimal). 7:30am would be entered as 7.5.

## Slide 89: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Capacitor
// Capacitor with control
New capacitor.Cap1 bus1=loadbus2 phases=3 kvar=600 kv=12.47
New capcontrol.Cap1Ctrl element=line.line3 terminal=1 capacitor=Cap1
~ type=current ctratio=1 ONsetting=60 OFFsetting=55 delay=2
OpenDSS Code:
Explanation:
delay
Specifies the time delay, in seconds, from when the control is armed before it sends out the switching command to turn the capacitor ON.

## Slide 90: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Regulator
// Regulator for DG
New transformer.reg1 phases=3 windings=2
~ buses=(loadbus3 regbus) conns='wye wye' kvs=(12.47 12.47) kvas=(8000 8000) XHL=1
// Regulator Control definitions
New regcontrol.subxfrmCtrl transformer=subxfrm winding=2 vreg=125
~ band=3 ptratio=60 delay=10
New regcontrol.reg1Ctrl transformer=reg1 winding=2 vreg=122 band=3
~ ptratio=60 delay=15
OpenDSS Code:
Explanation:
New Transformer.reg1
Defines a transformer named reg1.
phases
Specifies the number of phases.
windings
Specifies the number of windings.

## Slide 91: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Regulator
// Regulator for DG
New transformer.reg1 phases=3 windings=2
~ buses=(loadbus3 regbus) conns='wye wye' kvs=(12.47 12.47) kvas=(8000 8000) XHL=1
// Regulator Control definitions
New regcontrol.subxfrmCtrl transformer=subxfrm winding=2 vreg=125
~ band=3 ptratio=60 delay=10
New regcontrol.reg1Ctrl transformer=reg1 winding=2 vreg=122 band=3
~ ptratio=60 delay=15
OpenDSS Code:
Explanation:
kvs=(12.47 12.47)
buses=(loadbus3 regbus)
An array specifying the names of buses to which the windings are connected. Winding1 of transformer is connected to loadbus3, winding2 is connected to regubus.
conns='wye wye'
Specifies an array of connections for winding1 and winding2.
Specifies an array of kV ratings for winding1 and winding2.

## Slide 92: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Regulator
// Regulator for DG
New transformer.reg1 phases=3 windings=2
~ buses=(loadbus3 regbus) conns='wye wye' kvs=(12.47 12.47) kvas=(8000 8000) XHL=1
// Regulator Control definitions
New regcontrol.subxfrmCtrl transformer=subxfrm winding=2 vreg=125
~ band=3 ptratio=60 delay=10
New regcontrol.reg1Ctrl transformer=reg1 winding=2 vreg=122 band=3
~ ptratio=60 delay=15
OpenDSS Code:
Explanation:
kvas=(8000 8000)
Specifies an array of base kVA rating for winding1 and winding2.
XHL (or X12)
Specifies the percent reactance high‐to‐low (winding 1 to winding 2).

## Slide 93: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Regulator
// Regulator for DG
New transformer.reg1 phases=3 windings=2
~ buses=(loadbus3 regbus) conns='wye wye' kvs=(12.47 12.47) kvas=(8000 8000) XHL=1
// Regulator Control definitions
New regcontrol.subxfrmCtrl transformer=subxfrm winding=2 vreg=125
~ band=3 ptratio=60 delay=10
New regcontrol.reg1Ctrl transformer=reg1 winding=2 vreg=122 band=3
~ ptratio=60 delay=15
OpenDSS Code:
Explanation:
New regcontrol.subxfrmCtrl
Defines a regulator control object named subxfrmCtrl.
winding
Specifies the number of the winding of the transformer that the RegControl is monitoring. 1 or 2, typically.
transformer
Specifies the name of transformer to which the RegControl is connected.

## Slide 94: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Regulator
// Regulator for DG
New transformer.reg1 phases=3 windings=2
~ buses=(loadbus3 regbus) conns='wye wye' kvs=(12.47 12.47) kvas=(8000 8000) XHL=1
// Regulator Control definitions
New regcontrol.subxfrmCtrl transformer=subxfrm winding=2 vreg=125
~ band=3 ptratio=60 delay=10
New regcontrol.reg1Ctrl transformer=reg1 winding=2 vreg=122 band=3
~ ptratio=60 delay=15
OpenDSS Code:
Explanation:
band
Specifies the bandwidth, in VOLTS, for the controlled bus. Default is 3.0
vreg
Specifies the voltage regulator setting, in VOLTS, for the winding being controlled.

## Slide 95: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Regulator
// Regulator for DG
New transformer.reg1 phases=3 windings=2
~ buses=(loadbus3 regbus) conns='wye wye' kvs=(12.47 12.47) kvas=(8000 8000) XHL=1
// Regulator Control definitions
New regcontrol.subxfrmCtrl transformer=subxfrm winding=2 vreg=125
~ band=3 ptratio=60 delay=10
New regcontrol.reg1Ctrl transformer=reg1 winding=2 vreg=122 band=3
~ ptratio=60 delay=15
OpenDSS Code:
Explanation:
delay
Specifies the time delay, in seconds, from when the voltage goes out of band to when the tap changing begins. This is used to determine which regulator control will act first. Default is 15.
ptratio
Specifies the ratio of the PT that converts the controlled winding voltage to the regulator voltage. Default is 60. If the winding is Wye, the line‐to‐neutral voltage is used. Else, the line‐to‐line voltage is used.

## Slide 96: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Wind generator
// Define a wind generator of 8MW
New generator.gen1 bus1=regbus kV=12.47 kW=8000 pf=1 conn=delta
~ duty=wind Model=1
OpenDSS Code:
Explanation:
A Generator is a Power Conversion element similar to a Load object. Its rating is basically defined by its nominal kW and PF or its kW and kvar. Then it may be modified by a number of multipliers, including the global circuit load multiplier, yearly load shape, daily load shape, and a dutycycle load shape.
New generator.gen1
Defines a generator object named gen1.
bus1
Specifies the name of bus to which the generator is connected.

## Slide 97: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Wind generator
// Define a wind generator of 8MW
New generator.gen1 bus1=regbus kV=12.47 kW=8000 pf=1 conn=delta
~ duty=wind Model=1
OpenDSS Code:
Explanation:
kW
Specifies the nominal kW for generator. Total of all phases.
kV
Specifies the Base voltage for generator. For 2‐ or 3‐phase generators, it is specified in phase‐to-phase kV.
For all other generators, it is specified in the actual kV across the generator branch. If the generator is wye (star) connected, specify the phase‐to‐neutral (L‐N) kV. If the generator is delta or phase‐to-phase connected, specify the phase‐to‐phase (L‐L) kV.
pf
Specifies the nominal power factor for generator.

## Slide 98: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Wind generator
// Define a wind generator of 8MW
New generator.gen1 bus1=regbus kV=12.47 kW=8000 pf=1 conn=delta
~ duty=wind Model=1
OpenDSS Code:
Explanation:
conn
Specifies the winding connection of the generator. {wye | y | LN} for Wye (Line‐Neutral) connection; {delta | LL} for Delta (Line‐Line) connection. Default = wye.
duty
Specifies the name of Duty cycle load shape. Defaults to Daily load shape if not defined.
Model
An integer defining how the generator will vary with voltage. Presently defined models are:
…

## Slide 99: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Wind generator
// Define a wind generator of 8MW
New generator.gen1 bus1=regbus kV=12.47 kW=8000 pf=1 conn=delta
~ duty=wind Model=1
OpenDSS Code:
Explanation:
Model
…
1: Generator injects a constant kW at specified power factor.
2: Generator is modeled as a constant admittance.
3: Const kW, constant kV. Somewhat like a conventional transmission power flow P‐V generator.
4: Const kW, Fixed Q (Q never varies).
5: Const kW, Fixed Q(as a constant reactance).
6: Compute load injection from User‐written Model.
7: Constant kW, kvar, but current is limited when voltage is below Vminpu.

## Slide 100: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Monitor
// Define some monitors so we can see what's happening
New Monitor.gen1 element=generator.gen1 terminal=1 mode=1
New Monitor.loadbus2 load.load2 1 mode=0
New Monitor.line3 line.line3 1 mode=48
New Energymeter.em1 line.line1
OpenDSS Code:
Explanation:
A monitor is a circuit element that is connected to a terminal of another circuit element. It takes a sample when instructed, recording the time and the complex values of voltage and current, or power, at all phases.
New Monitor.gen1
Defines a monitor object named gen1.
element
Specify the name of an existing circuit element to which the monitor is connected.

## Slide 101: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Monitor
// Define some monitors so we can see what's happening
New Monitor.gen1 element=generator.gen1 terminal=1 mode=1
New Monitor.loadbus2 load.load2 1 mode=0
New Monitor.line3 line.line3 1 mode=48
New Energymeter.em1 line.line1
OpenDSS Code:
Explanation:
mode
An integer bitmask code to describe what the monitor will save. Monitors can save two basic types of quantities: 1) Voltage and current; 2) Power. The Mode codes are defined as follows:
0: Standard mode - V and I, each phase, complex
1: Power each phase, complex (kw and kvars)
…
terminal
Specifies the number of the terminal to which the monitor is connected.

## Slide 102: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Monitor
// Define some monitors so we can see what's happening
New Monitor.gen1 element=generator.gen1 terminal=1 mode=1
New Monitor.loadbus2 load.load2 1 mode=0
New Monitor.line3 line.line3 1 mode=48
New Energymeter.em1 line.line1
OpenDSS Code:
Explanation:
mode
…
2: Transformer taps (connect Monitor to a transformer winding)
3: State variables (connect Monitor to a Power conversion Element)
4: Flicker level and severity index (Pst) for voltages.
5: Solution variables (Iterations, etc). Normally, these would be actual phasor quantities from solution.
6: Capacitor Switching
…

## Slide 103: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Monitor
// Define some monitors so we can see what's happening
New Monitor.gen1 element=generator.gen1 terminal=1 mode=1
New Monitor.loadbus2 load.load2 1 mode=0
New Monitor.line3 line.line3 1 mode=48
New Energymeter.em1 line.line1
OpenDSS Code:
Explanation:
mode
…
+16: Sequence components: V012, I012
+32: Magnitude only
+64: Positive Sequence only or Average of phases, if not 3 phases.
For example, Mode=33 (33=1+32) will save the magnitude of the power (kVA) only in each phase. Mode=112 (112=0+16+32+64) saves Positive sequence voltages and currents, magnitudes only.

## Slide 104: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Energymeter
// Define some monitors so we can see what's happening
New Monitor.gen1 element=generator.gen1 terminal=1 mode=1
New Monitor.loadbus2 load.load2 1 mode=0
New Monitor.line3 line.line3 1 mode=48
New Energymeter.em1 line.line1
OpenDSS Code:
Explanation:
New Energymeter.em1
Defines an energymeter object named em1.
line.line1
The above code is the same as: Element=line.line1
It designates the name of an existing circuit element to which the Enegymeter is connected.
* An EnergyMeter object is an intelligent meter connected to a terminal of a circuit element. It simulates the behavior of an actual energy meter.

## Slide 105: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
Set voltagebases=(115 12.47 .48)
Defines legal bus voltage bases for this circuit. Enter an array of the legal voltage bases, in phase‐to‐phase voltages. In this case, three voltage bases are defined, 115kV, 12.47kV and 0.48kV.
The voltage level can be selected from the following values: .208, .480, 12.47, 24.9, 34.5, 115.0, 230.0

## Slide 106: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
Calcvoltagebases
Estimates the voltage base for each bus based on the array of voltage bases defined with a "Set Voltagebases=..." command. The voltage base for each bus is then set to the nearest voltage base specified in the voltage base array.
ControlMode
Specifies the Control mode for the solution. {OFF | STATIC |EVENT | TIME}, Default is "STATIC".
The detailed meanings are as follows:
…

## Slide 107: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
ControlMode
…
STATIC = Time does not advance. Control actions are executed in order of shortest time to act until all actions are cleared from the control queue.
EVENT = solution is event driven. Only the control actions nearest in time are executed and the time is advanced automatically to the time of the event.
TIME = solution is time driven. Control actions are executed when the time for the pending action is reached or surpassed.

## Slide 108: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
Mode
Specifies the solution mode for the active circuit. Mode can be one of snap, daily, direct, dutycycle, dynamics, faultstudy, harmonics, or yearly.
Mode=Snap:
Solve a single snapshot power flow for the present conditions. Loads are modified only by the global load multiplier (LoadMult) and the growth factor for the present year (Year).
…

## Slide 109: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
Mode
…
Mode=Daily:
Do a series of solutions following the daily load curves. The Stepsize defaults to 3600 sec (1 hr).
Mode=Direct:
Solve a single snapshot solution using an admittance model of all loads. This is noniterative; just a direct solution using the currently specified voltage and current sources.
…

## Slide 110: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
Mode
…
Mode=Dutycycle:
The solver follows the duty cycle curves with the time increment specified.
Mode=Dynamics:
Sets the solution mode for a dynamics solution. Must be preceded by a successful power flow solution so that the machines can be initialized.
…

## Slide 111: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
Mode
…
Mode=FaultStudy:
Do a full fault study solution, determining the Thevenin equivalents for each bus in the active circuit. Prepares all the data required to produce fault study report under the Show Fault command.
Mode=Harmonics:
Sets the solution mode for a Harmonics solution. Must be preceded by a successful power flow solution so that the machines and harmonics sources can be initialized.
Loads are converted to harmonic current sources and initialized based on the power flow solution according to the Spectrum object associated with each Load.
…

## Slide 112: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
Mode
…
Mode=Yearly:
Do a solution following the yearly load curves. The solution is repeated as many times as the specified by the Number=option. Each load then follows its yearly load curve. Load is determined solely by the yearly load curve and the growth multiplier.

## Slide 113: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
Set voltagebases=(115 12.47 .48)
Calcvoltagebases
Set controlmode=time
Set mode=dutycycle number=86400 hour=0 stepsize=1 sec=0
Solve
OpenDSS Code:
Explanation:
number
Specifies the number of time steps or solutions to run.
hour
Sets the hour to be used for the start time of the solution of the active circuit.
stepsize
Sets the time step size for the solution of the active circuit. Default unit is sec.
sec
Sets the seconds from the hour for the start time for the solution of the active circuit.

## Slide 114: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
// Show some results
Plot monitor, object=loadbus2
Visualize element=Line.line1 what=powers
Plot profile
OpenDSS Code:
Explanation:
plot
Displays a variety of results in a variety of manners on graphs.
monitor
Specifies that the type to be plotted is monitor. The Monitor plot plots one or more channels from a Monitor element.
object
Specifies what object to plot.
[metername for Zone plot | Monitor name | File Name for General bus data or Circuit branch data].

## Slide 115: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
// Show some results
Plot monitor, object=loadbus2
Visualize element=Line.line1 what=powers
Plot profile
OpenDSS Code:
Explanation:
channel
Specifies an array of channel numbers for monitor plot. More than one monitor channel can be plotted on the same graph. Example: Channels=[1, 3, 5]
visiualize
Shows the currents, voltages, or powers for selected element on a drawing in phasor quantities.

## Slide 116: Case II: Time-series Power Flow
ECpE Department
Build OpenDSS Model – Solve
// Show some results
Plot monitor, object=loadbus2
Visualize element=Line.line1 what=powers
Plot profile
OpenDSS Code:
Explanation:
element
Specifies the names of elements to be visualized. It should follow the following format:
element=full_element_name (i.e., class.name).
what
Specifies the what quantity to be visualized.
It can be the following item: currents, voltages, powers.
plot profile
Plot voltage profiles.

## Slide 117: Contents
ECpE Department
Static Snapshot Case
Time-series Static Case
Fault and Dynamic Case

## Slide 118: Case III: Fault and Dynamic
ECpE Department
Circuit
4 reclosers
1 relay
2 fuses
1 induction motor
7 loads
12 buses
1 voltage source
2 transformers
1 voltage regulator bank with control
3 capacitor banks
7 line segments
From 0 to 0.3 second, the circuit is in a normal status (no fault).
At t=0.3 second, a 0.21-second temporary SLG (Phase A) fault occurs at Bus B3.
Sensing the undervoltages and overcurrents, the Relay operates 0.1 s later (at t=0.4 second), isolating the induction motor.
Since the time duration of the fault is 0.21 s, the fault still exists. Therefore, the recloser rec1 disconnects line L3 0.11s later (at t=0.51 second). Also, almost at the same time, the temporary fault disappears.
After 0.5 seconds (at t=1.01 second), the recloser reconnects line L3.

## Slide 119: Case III: Fault and Dynamic
ECpE Department
OpenDSS files
17 files
Define capacitor banks
Define fault
Define fuse
Define induction motor
Define line segment
Define line configuration
Define load
Define loadshape
Define Master file
Define monitors
Define reclosers
Define regulator control
Define relay
Define a file to perform dynamic analysis
Define operating curves for relay, recloser and fuses
Define transformers
Define voltage source

## Slide 120: Case III: Fault and Dynamic
ECpE Department
Run.dss file
It is the main file which is defined to perform dynamic analysis.
Two steps to perform dynamic analysis:
  Run static power flow to obtain the initialization for dynamic simulation
  Perform the dynamic simulation
Redirect "Master.DSS" !Compile
New Monitor.Mtime Vsource.source mode=5 ! solution time monitor
Set Maxcontroliter=20
Set maxiterations=20
solve
OpenDSS Code (Initialization):
Explanation:
Redirect
Resets the current directory to Master.DSS file.

## Slide 121: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Redirect "Master.DSS" !Compile
New Monitor.Mtime Vsource.source mode=5 ! solution time monitor
Set Maxcontroliter=20
Set maxiterations=20
solve
OpenDSS Code (Initialization):
Explanation:
New Monitor.Mtime
Defines a monitor object named Mtime, which is used for collecting time information for plotting.
Vsource.source
It is equivalent with Element=Vsource.source
It specifies the Name of an existing circuit element to which the monitor is to be connected.

## Slide 122: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Redirect "Master.DSS" !Compile
New Monitor.Mtime Vsource.source mode=5 ! solution time monitor
Set Maxcontroliter=20
Set maxiterations=20
solve
OpenDSS Code (Initialization):
Explanation:
mode
Mode is an integer bitmask code to describe what the monitor will save. Monitors can save two basic types of quantities: 1) Voltage and current; 2) Power.
The Mode codes are defined as follows:
  0: Standard mode - V and I, each phase, complex
  1: Power each phase, complex (kw and kvars)
  2: Transformer taps (connect Monitor to a transformer winding)
  3: State variables (connect Monitor to a PCelement)
…

## Slide 123: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Redirect "Master.DSS" !Compile
New Monitor.Mtime Vsource.source mode=5 ! solution time monitor
Set Maxcontroliter=20
Set maxiterations=20
solve
OpenDSS Code (Initialization):
Explanation:
mode
…
  4: Flicker level and severity index (Pst) for voltages.
  5: Solution variables (Iterations, etc). Normally, these would be actual phasor quantities from solution.
  6: Capacitor Switching
+16: Sequence components: V012, I012
+32: Magnitude only
+64: Positive Sequence only or Average of phases, if not 3 phases.
For example, Mode=33 (33=1+32) will save the magnitude of the power (kVA) only in each phase.

## Slide 124: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Redirect "Master.DSS" !Compile
New Monitor.Mtime Vsource.source mode=5 ! solution time monitor
Set Maxcontroliter=20
Set maxiterations=20
solve
OpenDSS Code (Initialization):
Explanation:
Maxcontroliter
Sets the maximum control iterations per solution. Default is 10.
maxiterations
Also called Maxiter. Sets the maximum allowable iterations for power flow solutions. Default is 15.
Solve
Solves the circuit. Default mode is snapshot.

## Slide 125: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
Mode
Specifies the solution mode for the active circuit. Mode can be one of snap, daily, direct, dutycycle, dynamics, faultstudy, harmonics, yearly.
Mode=Snap:
Solve a single snapshot power flow for the present conditions. Loads are modified only by the global load multiplier (LoadMult) and the growth factor for the present year (Year).
…

## Slide 126: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
Mode
…
Mode=Daily:
Do a series of solutions following the daily load curves. The stepsize defaults to 3600 sec (1 hr).
Mode=Direct:
Solves a single snapshot solution using an admittance model of all loads. This is noniterative; just a direct solution using the currently specified voltage and current sources.
…

## Slide 127: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
Mode
…
Mode=Dutycycle:
Follows the duty cycle curves with the time increment specified.
Mode=Dynamics:
Sets the solution mode for a dynamics solution. Must be preceded by a successful power flow solution so that the machines can be initialized.
…

## Slide 128: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
Mode
…
Mode=FaultStudy:
Do a full fault study solution, determining the Thevenin equivalents for each bus in the active circuit. Prepares all the data required to produce fault study report under the Show Fault command.
…

## Slide 129: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
Mode
…
Mode=Harmonics:
Sets the solution mode for a Harmonics solution. Must be preceded by a successful power flow solution, so that the machines and harmonics sources can be initialized.
Loads are converted to harmonic current sources and initialized based on the power flow solution, according to the Spectrum object associated with each Load.
…

## Slide 130: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
Mode
…
Mode=Yearly:
Do a solution following the yearly load curves. The solution is repeated as many times as the specified by the Number=option. Each load then follows its yearly load curve. Load is determined solely by the yearly load curve and the growth multiplier.
number
Specifies the number of time steps in each solution.

## Slide 131: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
h
Also called stepsize. It sets the time step size for the solution of the active circuit. Default unit is second. Normally, this is specified for dynamic solution.
Solve number= 10000
Specifies the number of solutions in dynamic simulation to run.
Solve
Solves the circuit.

## Slide 132: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Set mode=dynamics number=1 h=0.000166667
solve
Solve number= 10000
get time
get number
OpenDSS Code (Perform Dynamic Simulation):
Explanation:
get number
Obtains number values of solutions in dynamic simulation.
get time
Obtains time values of solutions in dynamic simulation.

## Slide 133: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Plot monitor object= cb1 channels=(1, 3, 5)
Plot monitor object= cb1 channels=(7, 9, 11)
Plot monitor object= rec1 channels=(1, 3, 5)
Plot monitor object= F1 channels=(1, 3, 5)
OpenDSS Code (Plot Results):
Explanation:
monitor
Specifies that the type to be plotted is monitor. The Monitor plot plots one or more channels from a Monitor element.
plot
Displays a variety of results in a variety of manners on graphs.
object
Specifies what object to plot.
[metername for Zone plot | Monitor name | File Name for General bus data or Circuit branch data].

## Slide 134: Case III: Fault and Dynamic
ECpE Department
Run.dss file
Plot monitor object= cb1 channels=(1, 3, 5)
Plot monitor object= cb1 channels=(7, 9, 11)
Plot monitor object= rec1 channels=(1, 3, 5)
Plot monitor object= F1 channels=(1, 3, 5)
OpenDSS Code (Plot Results):
Explanation:
channel
Specifies the array of channel numbers for monitor plot. More than one monitor channel can be plotted on the same graph. Example: Channels=[1, 3, 5]

## Slide 135: Case III: Fault and Dynamic
ECpE Department
Master.dss file
Clear
New Circuit.NewModel
Redirect Vsource.dss
Redirect LineCode.dss
Redirect LoadShape.dss
Redirect TCC_Curve.dss
Redirect line.dss
Redirect Load.dss
Redirect Transformer.dss
Redirect RegControl.dss
Redirect Capacitor.dss
Redirect Fault.dss
Redirect IndMach012.dss
Redirect Relay.dss
Redirect Recloser.dss
Redirect Fuse.dss
Redirect Monitor.dss
Buscoords buscoords.dat
set voltagebases=(115 12.47 .48)
calcv
OpenDSS Code:

## Slide 136: Case III: Fault and Dynamic
ECpE Department
Vsource.dss file
Edit "Vsource.source" bus1=Bx basekv=115 pu=1.0475 angle=0 frequency=60 phases=3 MVAsc3=20000 MVAsc1=21000 x1r1=4 x0r0=3
OpenDSS Code:
Explanation:
Edit
Edits the object specified. In this case, the Vsource object named source is edited.
bus1
Specifies the bus to which Vsource is connected.
basekv
Specifies Base or rated Line‐to‐line kV of Vsource.
pu
Specifies the actual per unit at which the source is operating. It is assumed balanced for all phases.
Angle
Specifies Base angle, in degrees, of the first phase.

## Slide 137: Case III: Fault and Dynamic
ECpE Department
Vsource.dss file
Edit "Vsource.source" bus1=Bx basekv=115 pu=1.0475 angle=0 frequency=60 phases=3 MVAsc3=20000 MVAsc1=21000 x1r1=4 x0r0=3
OpenDSS Code:
Explanation:
frequency
Specifies the frequency of the source.
phases
Specifies the number of phases. Default = 3.0.
MVAsc3
Specifies the 3‐phase short circuit MVA.
MVAsc1
Specifies the 1‐phase short circuit MVA.
x1r1
Specifies the ratio of X1/R1. Default = 4.0.
x0r0
Specifies the ratio of X0/R0. Default = 3.0.

## Slide 138: Case III: Fault and Dynamic
ECpE Department
Linecode.dss file
New "LineCode.3x_336aa_1/0asn" nphases=3 baseFreq=60 normamps=396 emergamps=495 r1=0.05284 x1=0.12447 r0=0.14504 x0=0.41903 c1=3.30053 c0=1.43804 units=kft
…
OpenDSS Code:
Explanation:
LineCode.3x_336aa_1/0asn
Defines a linecode object named 3x_336aa_1/0asn.
nphases
Specifies the number of phases. Default = 3.
BaseFreq
Specifies the Base Frequency at which the impedance values are specified. Default = 60.0 Hz.
Normamps
Specifies the normal ampacity, in amps.
emergamps
Specifies the emergency ampacity, in amps.

## Slide 139: Case III: Fault and Dynamic
ECpE Department
Linecode.dss file
New "LineCode.3x_336aa_1/0asn" nphases=3 baseFreq=60 normamps=396 emergamps=495 r1=0.05284 x1=0.12447 r0=0.14504 x0=0.41903 c1=3.30053 c0=1.43804 units=kft
…
OpenDSS Code:
Explanation:
r1
Specifies the positive-sequence resistance, in ohms per unit length.
x1
Specifies the positive-sequence reactance, in ohms per unit length.
r0
Specifies the zero-sequence resistance, in ohms per unit length.
x0
Specifies the zero-sequence reactance, in ohms per unit length.

## Slide 140: Case III: Fault and Dynamic
ECpE Department
Linecode.dss file
New "LineCode.3x_336aa_1/0asn" nphases=3 baseFreq=60 normamps=396 emergamps=495 r1=0.05284 x1=0.12447 r0=0.14504 x0=0.41903 c1=3.30053 c0=1.43804 units=kft
…
OpenDSS Code:
Explanation:
c1
Specifies the positive-sequence capacitance, in nanofarads per unit length.
c0
Specifies the zero-sequence capacitance, in nanofarads per unit length.
units
Specifies the length units. If not specified, it is assumed that the units correspond to the length being used in the Line models.
{mi | km | kft | m | ft | in | cm}.

## Slide 141: Case III: Fault and Dynamic
ECpE Department
Lodeshape.dss file
New "LoadShape.wind2400" npts=2501 interval=0.000277778 csvfile=WPWind2400.csv action=normalize
OpenDSS Code:
Explanation:
New "LoadShape.wind2400"
Defines a loadshape object named wind2400.
interval
Specifies the time interval of the data, in Hr. Default=1.0. If the load shape has non‐uniformly spaced points, specify the interval as 0.0.
Npts
Specifies the number of points to expect when defining the curve.
csvfile
Specifies the name of a CSV file containing active power load shape data, one interval to a line.

## Slide 142: Case III: Fault and Dynamic
ECpE Department
Lodeshape.dss file
New "LoadShape.wind2400" npts=2501 interval=0.000277778 csvfile=WPWind2400.csv action=normalize
OpenDSS Code:
Explanation:
action
{Normalize | DblSave | SngSave} After defining load curve data, setting action=normalize will modify the multipliers, so that the peak is 1.0. The mean and std deviation are recomputed.
mean
Specifies the mean of the multiplier array.
stddev
Specifies the standard deviation of the multiplier array.

## Slide 143: Case III: Fault and Dynamic
ECpE Department
TCC_Curve.dss file
New "TCC_Curve.a" npts=15 C_array=(1.1, 1.3, 1.5, 2, 3, 4, 5, 6, 7, 8, 9, 10, 20, 50, 100, ) T_array=(7.1769, 2.2079, 1.234, 0.534, 0.2215, 0.134, 0.0965, 0.0769, 0.0653, 0.0578, 0.0528, 0.0492, 0.0378, 0.0346, 0.0342, )
OpenDSS Code:
Explanation:
A TCC_Curve object is defined similarly to Loadshape and Growthshape objects in that they all are defined by curves consisting of arrays of points.
New "TCC_Curve.a"
Defines a TCC_curve object named a.
Npts
Number of points to expect when defining the curve.

## Slide 144: Case III: Fault and Dynamic
ECpE Department
TCC_Curve.dss file
New "TCC_Curve.a" npts=15 C_array=(1.1, 1.3, 1.5, 2, 3, 4, 5, 6, 7, 8, 9, 10, 20, 50, 100, ) T_array=(7.1769, 2.2079, 1.234, 0.534, 0.2215, 0.134, 0.0965, 0.0769, 0.0653, 0.0578, 0.0528, 0.0492, 0.0378, 0.0346, 0.0342, )
OpenDSS Code:
Explanation:
C_Array
Specifies an array of current (or voltage or whatever) values corresponding to time values in T_Array.
T_Array
Specifies an array of time values in seconds. Typical array syntax:
t_array = (1, 2, 3, 4, ...)

## Slide 145: Case III: Fault and Dynamic
ECpE Department
Line.dss file
New "line.l1" bus1=B0 bus2=B1 linecode="Unbalanced 336 ACSR" length=10 units=kft
OpenDSS Code:
Explanation:
New Line.l1
Defines a line object named l1.
Phases
Specifies the number of phases. Default = 3.
Bus1
Specifies the name of bus for terminal 1.
Bus2
Specifies the name of bus for terminal 2.

## Slide 146: Case III: Fault and Dynamic
ECpE Department
Line.dss file
New "line.l1" bus1=B0 bus2=B1 linecode="Unbalanced 336 ACSR" length=10 units=kft
OpenDSS Code:
Explanation:
LineCode
Specifies the name of an existing LineCode object containing impedance definitions.
Length
Specifies the length multiplier to be applied to the impedance data.
Units
Specifies the length units. {none | mi | kft | km | m | Ft | in | cm}.

## Slide 147: Case III: Fault and Dynamic
ECpE Department
Load.dss file
New "Load.ldb0" bus1=B0 conn=wye phases=3 kW=0.1 pf=1 model=2 kV=12.47
OpenDSS Code:
Explanation:
New Load.ldb0
Defines a load object named ldb0.
bus1
Specifies the name of bus to which the load is connected.
conn
Specifies the connection of load. {wye | y | LN} for Wye (Line‐Neutral) connection; {delta | LL} for Delta (Line‐Line) connection. Default = wye.
phases
Specifies the number of phases of this load.
kw
Specifies the nominal active power, in kW, for the load. Total of all phases.

## Slide 148: Case III: Fault and Dynamic
ECpE Department
Load.dss file
New "Load.ldb0" bus1=B0 conn=wye phases=3 kW=0.1 pf=1 model=2 kV=12.47
OpenDSS Code:
Explanation:
pf
Specifies the nominal power factor for load. Negative PF is leading. Specify either PF or kvar. If both are specified, the last one specified takes precedence.
Model
An integer defining how the load will vary with voltage. The load models currently implemented are:
  1: Constant P and constant Q (Default): Commonly used for power flow studies,
  2: Constant Z (or constant impedance),
  3: Constant P and quadratic Q (),
  4: Exponential: and
  5: Constant I (or constant current magnitude),
…

## Slide 149: Case III: Fault and Dynamic
ECpE Department
Load.dss file
New "Load.ldb0" bus1=B0 conn=wye phases=3 kW=0.1 pf=1 model=2 kV=12.47
OpenDSS Code:
Explanation:
Model
…
  6: Constant P and fixed Q (at the nominal value)
  7: Constant P and quadratic Q (i.e., fixed reactance),
  8: ZIP
  "Constant" power value (either P or Q) may be modified by loadshape multipliers. "Fixed" power values are always the same.

## Slide 150: Case III: Fault and Dynamic
ECpE Department
Load.dss file
New "Load.ldb0" bus1=B0 conn=wye phases=3 kW=0.1 pf=1 model=2 kV=12.47
OpenDSS Code:
Explanation:
kV
Specifies the Base voltage for load. For 2‐ or 3‐phase loads, it is specified in phase‐to‐phase kV.
For all other loads, it is specified in the actual kV across the load branch. If the load is wye (star) connected, then specify phase‐to‐neutral (L‐N). If the load is delta or phase‐to‐phase connected, specify the phase‐to‐phase (L‐L) kV.

## Slide 151: Case III: Fault and Dynamic
ECpE Department
Transformer.dss file
New "Transformer.sub" phases=3 windings=2 buses=(bx, b0, ) conns=(delta, wye, ) kVs=(115, 12.47, ) kVAs=(20000, 20000, ) taps=(1, 1, ) Xhl=7
OpenDSS Code:
Explanation:
New "Transformer.sub"
Defines a transformer object named sub.
phases
windings
Specifies the number of windings. Default is 2.
Specifies the number of phases. Default is 3.
buses=(bx, b0, )
bus1:
Name of bus for terminal 1.
bus2:
Name of bus for terminal 2.
Specifies an array of names of buses to which the windings are connected. The above code equals: bus1=bx bus2=b0

## Slide 152: Case III: Fault and Dynamic
ECpE Department
Transformer.dss file
New "Transformer.sub" phases=3 windings=2 buses=(bx, b0, ) conns=(delta, wye, ) kVs=(115, 12.47, ) kVAs=(20000, 20000, ) taps=(1, 1, ) Xhl=7
OpenDSS Code:
Explanation:
conns=(delta, wye, )
Specifies an array of connections for windings. The connection of winding1 is ‘delta’. The connection of winding2 is ‘wye’.
kvs=(115, 12.47,)
Specifies an array of kV ratings for windings. The rated voltage of winding1 is 115 kV. The rated voltage of winding2 is 12.47kV.
kvas=(20000, 20000,)
Specifies an array of kVA ratings for windings. The base kVA rating of winding1 is 20000 kVA. The base kVA rating of winding2 is 20000kVA.

## Slide 153: Case III: Fault and Dynamic
ECpE Department
Transformer.dss file
New "Transformer.sub" phases=3 windings=2 buses=(bx, b0, ) conns=(delta, wye, ) kVs=(115, 12.47, ) kVAs=(20000, 20000, ) taps=(1, 1, ) Xhl=7
OpenDSS Code:
Explanation:
xhl
Specifies the percent reactance high‐to‐low (winding 1 to winding 2).
taps(1, 1, )
Specifies an array of tap positions for windings. The tap position of winding1 is 1. The tap position of winding2 is 1.

## Slide 154: Case III: Fault and Dynamic
ECpE Department
RegControl.dss file
New "RegControl.reg1a" transformer=Reg1a winding=2 vreg=119.9926 band=3 ptratio=60 delay=15 tapdelay=2 reversible=yes revvreg=119.9926 revband=3 CTprim=600 R=5 X=3 revR=5 revX=3
OpenDSS Code:
Explanation:
New "RegControl.reg1a"
Defines a regulator control object named reg1a.
winding
Specifies the number of the winding of the transformer that the RegControl is monitoring. 1 or 2, typically.
vreg
Specifies the voltage regulator setting, in volts, for the winding being controlled. Default is 120.0
transformer
Specifies the name of transformer to which the RegControl is connected.

## Slide 155: Case III: Fault and Dynamic
ECpE Department
RegControl.dss file
New "RegControl.reg1a" transformer=Reg1a winding=2 vreg=119.9926 band=3 ptratio=60 delay=15 tapdelay=2 reversible=yes revvreg=119.9926 revband=3 CTprim=600 R=5 X=3 revR=5 revX=3
OpenDSS Code:
Explanation:
band
Specifies the bandwidth, in volts, for the controlled bus. Default is 3.0
ptratio
Specifies the ratio of the PT that converts the controlled winding voltage to the regulator voltage. Default is 60. If the winding is Wye, the line‐to‐neutral voltage is used. Else, the line‐to‐line voltage is used.
delay
Specifies the time delay, in seconds, from when the voltage goes out of band to when the tap changing begins. This is used to determine which regulator control will act first. Default is 15.

## Slide 156: Case III: Fault and Dynamic
ECpE Department
RegControl.dss file
New "RegControl.reg1a" transformer=Reg1a winding=2 vreg=119.9926 band=3 ptratio=60 delay=15 tapdelay=2 reversible=yes revvreg=119.9926 revband=3 CTprim=600 R=5 X=3 revR=5 revX=3
OpenDSS Code:
Explanation:
tapdelay
Specifies the delay, in seconds, between tap changes. Default is 2. This is how long it takes between changes after the first change.
reversible
Indicates whether or not the regulator can be switched to regulate in the reverse direction. Default is No. {Yes |No*}
revvreg
Specifies the voltage setting, in volts, for operation in the reverse direction.

## Slide 157: Case III: Fault and Dynamic
ECpE Department
RegControl.dss file
New "RegControl.reg1a" transformer=Reg1a winding=2 vreg=119.9926 band=3 ptratio=60 delay=15 tapdelay=2 reversible=yes revvreg=119.9926 revband=3 CTprim=600 R=5 X=3 revR=5 revX=3
OpenDSS Code:
Explanation:
revband
Specifies the bandwidth for operating in the reverse direction.
CTprim
Specifies the rating, in Amperes, of the primary CT rating for converting the line amps to control amps. The typical default secondary ampere rating is 0.2 Amps.
R
Specifies the R setting on the line drop compensator in the regulator, in volts.

## Slide 158: Case III: Fault and Dynamic
ECpE Department
RegControl.dss file
New "RegControl.reg1a" transformer=Reg1a winding=2 vreg=119.9926 band=3 ptratio=60 delay=15 tapdelay=2 reversible=yes revvreg=119.9926 revband=3 CTprim=600 R=5 X=3 revR=5 revX=3
OpenDSS Code:
Explanation:
X
Specifies the X setting on the line drop compensator in the regulator, in volts.
revR
Specifies the R line drop compensator setting for reverse direction, in volts.
revX
Specifies the X line drop compensator setting for reverse direction, in volts.

## Slide 159: Case III: Fault and Dynamic
ECpE Department
Capacitor.dss file
New "Capacitor.c1" conn=wye bus1=B1 phases=3 kvar=( 600) kv=12.47
OpenDSS Code:
Explanation:
New "Capacitor.c1"
Defines a capacitor object named c1.
Bus1
Specifies the name of bus to which the first bus is connected.
conn
Specifies the connection of bank. One of {wye | ln} for wye connected banks or {delta | ll} for delta (line-line) connected banks.
phases
Specifies the number of phases.

## Slide 160: Case III: Fault and Dynamic
ECpE Department
Capacitor.dss file
New "Capacitor.c1" conn=wye bus1=B1 phases=3 kvar=( 600) kv=12.47
OpenDSS Code:
Explanation:
kVAR
Specifies the rated kvar at rated kV, total of all phases. Each phase is assumed equal.
kV
Specifies the kV rating of the capacitor bank. For Phases=2 or Phases=3, enter line‐to‐line (phase‐to‐phase) rated voltage. For all other numbers of phases, enter actual can rating. (For Delta connection this is always line‐to‐line rated voltage).

## Slide 161: Case III: Fault and Dynamic
ECpE Department
Fault.dss file
New "Fault.thefault" bus1=B3.1 bus2=B3.0 phases=1 r=0.0001 ONtime=.3 temporary=yes
OpenDSS Code:
Explanation:
New "Fault.thefault"
Defines a fault object named thefault.
bus1
Specifies the name of first bus the resistor is connected to.
bus2
Specifies the name of second bus the resistor is connected to.
phases
Specifies the number of phases. Default is 1.
A fault object is nothing more than a resistor network with a variety of configurations.

## Slide 162: Case III: Fault and Dynamic
ECpE Department
Fault.dss file
New "Fault.thefault" bus1=B3.1 bus2=B3.0 phases=1 r=0.0001 ONtime=.3 temporary=yes
OpenDSS Code:
Explanation:
r
Specifies the resistance of each phase, in ohms. Default is 0.0001.
ontime
Specifies the time, in seconds, at which the fault is established for time varying simulations.
Temporary
Designates whether the fault is temporary or not.
{Yes | No} Default is No.

## Slide 163: Case III: Fault and Dynamic
ECpE Department
IndMach012.dss file
New "IndMach012.Motor1" bus1=Bg2 kW=1200 conn=delta kVA=1500.000 H=6 duty=Wind2400 purs=0.048 puxs=0.075 purr=0.018 puxr=0.12 puxm=3.8 slip=0.02 SlipOption=variableslip kv=0.48
OpenDSS Code:
Explanation:
INDMACH012 is an induction machine (asynchronous machine) model.
New "IndMach012.Motor1"
Defines an IndMach012 object named Motor1.
bus1
Specifies the name of bus to which the machine is connected.
kW
Specifies the shaft power, in kW, for the Induction Machine. A positive value denotes power for a load. Negative value denotes an induction generator. Total of all phases.
https://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=1626370

## Slide 164: Case III: Fault and Dynamic
ECpE Department
IndMach012.dss file
New "IndMach012.Motor1" bus1=Bg2 kW=1200 conn=delta kVA=1500.000 H=6 duty=Wind2400 purs=0.048 puxs=0.075 purr=0.018 puxr=0.12 puxm=3.8 slip=0.02 SlipOption=variableslip kv=0.48
OpenDSS Code:
Explanation:
kVA
Specifies the rated kVA for the machine.
H
Specifies the per unit mass constant of the machine. In MW-sec/MVA. Default is 1.0.
conn
Specifies the connection of stator: Delta or Wye. Default is Delta.
duty
Specifies the load shape to use for simulations.

## Slide 165: Case III: Fault and Dynamic
ECpE Department
IndMach012.dss file
New "IndMach012.Motor1" bus1=Bg2 kW=1200 conn=delta kVA=1500.000 H=6 duty=Wind2400 purs=0.048 puxs=0.075 purr=0.018 puxr=0.12 puxm=3.8 slip=0.02 SlipOption=variableslip kv=0.48
OpenDSS Code:
Explanation:
puxs
Specifies the per unit stator leakage reactance. Default is 0.106.
purr
Specifies the per unit rotor resistance. Default is 0.007.
purs
Specifies the per unit stator resistance. Default is 0.0053.
puxr
Specifies the per unit rotor leakage reactance. Default is 0.12.

## Slide 166: Case III: Fault and Dynamic
ECpE Department
IndMach012.dss file
New "IndMach012.Motor1" bus1=Bg2 kW=1200 conn=delta kVA=1500.000 H=6 duty=Wind2400 purs=0.048 puxs=0.075 purr=0.018 puxr=0.12 puxm=3.8 slip=0.02 SlipOption=variableslip kv=0.48
OpenDSS Code:
Explanation:
slip
Specifies the initial slip value. Default is 0.007.
SlipOption
Specifies the option for slip model. One of {fixedslip | variableslip* }. Variable slip is the default and slip will be computed to satisfy the power specification. If fixed slip, kW is computed to match the slip specification.
puxm
Specifies the per unit magnetizing reactance. Default is 4.0.

## Slide 167: Case III: Fault and Dynamic
ECpE Department
IndMach012.dss file
New "IndMach012.Motor1" bus1=Bg2 kW=1200 conn=delta kVA=1500.000 H=6 duty=Wind2400 purs=0.048 puxs=0.075 purr=0.018 puxr=0.12 puxm=3.8 slip=0.02 SlipOption=variableslip kv=0.48
OpenDSS Code:
Explanation:
kv
Specifies the Base voltage for the induction machine. For 2- or 3-phase generators, specified in phase-to-phase kV. For all other generators, the actual kV across the generator branch. If wye (star) connected, specify the phase-to-neutral (L-N) kV. If delta or phase-to-phase connected, specify the phase-to-phase (L-L) kV.

## Slide 168: Case III: Fault and Dynamic
ECpE Department
Relay.dss file
New "Relay.mfrov/uv" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=voltage kvbase=0.48 Delay=0
New "Relay.mfr46" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=46 46BaseAmps=1800 46%Pickup=20 46isqt=1 Delay=0.1
New "Relay.mfr47" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=47 kvbase=0.48 47%Pickup=2 Delay=0.1
OpenDSS Code:
Explanation:
New "Relay.mfrov/uv"
Defines a relay object named mfrov/uv.
MonitoredObj
Specifies the full object name of the circuit element, typically a line, transformer, load, or generator, to which the relay's PT and/or CT are connected. This is the "monitored" element. There is no default; must be specified.
Relays are used to control distribution circuit breakers. The inverse time overcurrent characteristics is commonly used. An inverse time-current characteristic means that the relay will operate faster with increased current.

## Slide 169: Case III: Fault and Dynamic
ECpE Department
Relay.dss file
OpenDSS Code:
Explanation:
type
Specifies the type of the relay. Voltage: undervoltage and overvoltage protection.
46: negative sequence current protection.
47: negative sequence voltage protection.
MonitoredTerm
Specifies the number of the terminal of the circuit element to which the Relay is connected. 1 or 2, typically. Default is 1.
New "Relay.mfrov/uv" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=voltage kvbase=0.48 Delay=0
New "Relay.mfr46" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=46 46BaseAmps=1800 46%Pickup=20 46isqt=1 Delay=0.1
New "Relay.mfr47" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=47 kvbase=0.48 47%Pickup=2 Delay=0.1

## Slide 170: Case III: Fault and Dynamic
ECpE Department
Relay.dss file
OpenDSS Code:
Explanation:
kvase
Specifies the voltage base (kV) for the relay. Specify line‐line for 3 phase devices); line-neutral for 1‐phase devices.
delay
Specifies the trip time delay, in seconds, for definite time relays.
46BaseAmps
Specifies the Base current, in amps, for 46 relay (neg seq current).
New "Relay.mfrov/uv" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=voltage kvbase=0.48 Delay=0
New "Relay.mfr46" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=46 46BaseAmps=1800 46%Pickup=20 46isqt=1 Delay=0.1
New "Relay.mfr47" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=47 kvbase=0.48 47%Pickup=2 Delay=0.1

## Slide 171: Case III: Fault and Dynamic
ECpE Department
Relay.dss file
OpenDSS Code:
Explanation:
46%Pickup
Specifies the percent pickup current for 46 relay (neg seq current). Default is 20.0.
47%Pickup
Specifies the percent voltage pickup for 47 relay (Neg seq voltage). Default is 2.
46isqt
Specifies the negative-sequence I‐squared‐t trip value for 46 relay. Default is 1 (trips in 1 sec for 1 per unit neg-seq current). Should be 1 to 99.
New "Relay.mfrov/uv" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=voltage kvbase=0.48 Delay=0
New "Relay.mfr46" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=46 46BaseAmps=1800 46%Pickup=20 46isqt=1 Delay=0.1
New "Relay.mfr47" MonitoredObj=line.MotorLeads MonitoredTerm=1 type=47 kvbase=0.48 47%Pickup=2 Delay=0.1

## Slide 172: Case III: Fault and Dynamic
ECpE Department
Recloser.dss file
New "Recloser.cb1" MonitoredObj=Line.L1 MonitoredTerm=1 NumFast=4 PhaseFast=Ext_Inv PhaseDelayed=Ext_Inv PhaseTrip=800 TDPhFast=1 TDPhDelayed=1 PhaseInst=2400 GroundFast=Ext_Inv GroundDelayed=Ext_Inv GroundTrip=800 TDGrFast=1 TDGrDelayed=1 GroundInst=1200 Shots=4 RecloseIntervals=(0.5, 2, 2, )
OpenDSS Code:
A recloser is a self-controlled device for automatically interrupting and reclosing an alternating-current circuit, with a predetermined sequence of opening and reclosing followed by resetting, hold closed, or lockout.
http://c03.apogee.net/contentplayer/?coursetype=foe&utilityid=mp&id=4488

## Slide 173: Case III: Fault and Dynamic
ECpE Department
Recloser.dss file
New "Recloser.cb1" MonitoredObj=Line.L1 MonitoredTerm=1 NumFast=4 PhaseFast=Ext_Inv PhaseDelayed=Ext_Inv PhaseTrip=800 TDPhFast=1 TDPhDelayed=1 PhaseInst=2400 GroundFast=Ext_Inv GroundDelayed=Ext_Inv GroundTrip=800 TDGrFast=1 TDGrDelayed=1 GroundInst=1200 Shots=4 RecloseIntervals=(0.5, 2, 2, )
OpenDSS Code:
Explanation:
New "Recloser.cb1"
Defines a recloser object named cb1.
MonitoredTerm
Specifies the number of the terminal of the circuit element to which the Recloser is connected. 1 or 2, typically. Default is 1.
MonitoredObj
Specifies the full object name of the circuit element, typically a line, transformer, load, or generator, to which the Recloser's PT and/or CT are connected. This is the "monitored" element. There is no default; must be specified.

## Slide 174: Case III: Fault and Dynamic
ECpE Department
Recloser.dss file
New "Recloser.cb1" MonitoredObj=Line.L1 MonitoredTerm=1 NumFast=4 PhaseFast=Ext_Inv PhaseDelayed=Ext_Inv PhaseTrip=800 TDPhFast=1 TDPhDelayed=1 PhaseInst=2400 GroundFast=Ext_Inv GroundDelayed=Ext_Inv GroundTrip=800 TDGrFast=1 TDGrDelayed=1 GroundInst=1200 Shots=4 RecloseIntervals=(0.5, 2, 2, )
OpenDSS Code:
Explanation:
Specifies the number of Fast (fuse saving) operations. Default is 1.
Fast and delayed operation: The trip operations of the recloser can be all fast, all delayed, or any combination of fast operations, followed by delayed operations up to a maximum total of four. Fast operations clear temporary faults before branch line fuses are damaged. Delayed operations allow time for fuses or other downline protective devices to clear to limit permanent faults to the smallest section of line.
NumFast
phaseFast
Specifies the name of the TCC Curve object that determines the Phase Fast trip.

## Slide 175: Case III: Fault and Dynamic
ECpE Department
Recloser.dss file
New "Recloser.cb1" MonitoredObj=Line.L1 MonitoredTerm=1 NumFast=4 PhaseFast=Ext_Inv PhaseDelayed=Ext_Inv PhaseTrip=800 TDPhFast=1 TDPhDelayed=1 PhaseInst=2400 GroundFast=Ext_Inv GroundDelayed=Ext_Inv GroundTrip=800 TDGrFast=1 TDGrDelayed=1 GroundInst=1200 Shots=4 RecloseIntervals=(0.5, 2, 2, )
OpenDSS Code:
Explanation:
PhaseTrip
Specifies a Multiplier or actual phase amps for the phase TCC curve. Defaults to 1.0.
PhaseDelayed
Specifies the name of the TCC Curve object that determines the Phase Delayed trip.
TDPhFast
Specifies a time dial for Phase Fast trip curve. It is a multiplier on time axis of specified curve. Default=1.0.
TDPhDelayed
Specifies a time dial for Phase Delayed trip curve. It is a multiplier on time axis of specified curve. Default=1.0.

## Slide 176: Case III: Fault and Dynamic
ECpE Department
Recloser.dss file
New "Recloser.cb1" MonitoredObj=Line.L1 MonitoredTerm=1 NumFast=4 PhaseFast=Ext_Inv PhaseDelayed=Ext_Inv PhaseTrip=800 TDPhFast=1 TDPhDelayed=1 PhaseInst=2400 GroundFast=Ext_Inv GroundDelayed=Ext_Inv GroundTrip=800 TDGrFast=1 TDGrDelayed=1 GroundInst=1200 Shots=4 RecloseIntervals=(0.5, 2, 2, )
OpenDSS Code:
Explanation:
PhaseInst
Specifies the actual amps (Current relay) or kW (reverse power relay) for instantaneous phase trip which is assumed to happen in 0.01 sec + Delay Time. Default is 0.0, which signifies no instantaneous trip.
GroundFast
Specifies the name of the TCC Curve object that determines the Ground Fast trip.
GroundDelayed
Specifies the name of the TCC Curve object that determines the Ground Delayed trip.

## Slide 177: Case III: Fault and Dynamic
ECpE Department
Recloser.dss file
New "Recloser.cb1" MonitoredObj=Line.L1 MonitoredTerm=1 NumFast=4 PhaseFast=Ext_Inv PhaseDelayed=Ext_Inv PhaseTrip=800 TDPhFast=1 TDPhDelayed=1 PhaseInst=2400 GroundFast=Ext_Inv GroundDelayed=Ext_Inv GroundTrip=800 TDGrFast=1 TDGrDelayed=1 GroundInst=1200 Shots=4 RecloseIntervals=(0.5, 2, 2, )
OpenDSS Code:
Explanation:
GroundTrip
Specifies a multiplier or actual ground amps (3I0) for the ground TCC curve. Defaults to 1.0.
TDGrFast
Specifies the time dial for Ground Fast trip curve. It is a multiplier on time axis of specified curve. Default=1.0.
TDGrDelayed
Specifies the time dial for Ground Delayed trip curve. It is a multiplier on time axis of specified curve. Default=1.0.

## Slide 178: Case III: Fault and Dynamic
ECpE Department
Recloser.dss file
New "Recloser.cb1" MonitoredObj=Line.L1 MonitoredTerm=1 NumFast=4 PhaseFast=Ext_Inv PhaseDelayed=Ext_Inv PhaseTrip=800 TDPhFast=1 TDPhDelayed=1 PhaseInst=2400 GroundFast=Ext_Inv GroundDelayed=Ext_Inv GroundTrip=800 TDGrFast=1 TDGrDelayed=1 GroundInst=1200 Shots=4 RecloseIntervals=(0.5, 2, 2, )
OpenDSS Code:
Explanation:
GroundInst
Specifies the actual amps for instantaneous ground trip which is assumed to happen in 0.01 sec + Delay Time. Default is 0.0, which signifies no instantaneous trip.
shots
Specifies the total Number of fast and delayed shots to lockout. Default is 4. This is one more than the number of reclose intervals.
RecloseIntervals
Specifies an array of reclose intervals. Default for Recloser is (0.5, 2.0, 2.0) seconds.

## Slide 179: Case III: Fault and Dynamic
ECpE Department
Fuse.dss file
New "Fuse.f1" MonitoredObj=Line.L6 MonitoredTerm=1 FuseCurve=Klink RatedCurrent=65
OpenDSS Code:
Fuses have elements that melt if enough current flows through it for enough time.
Industry standards specify two types of expulsion fuses.
  K-type: fast fuse with speed ratio of 6-8
  T-type: slower fuse with speed ratio of 10-13
The speed ratio is the ratio of
  The melting current at 0.1 second to
  the melting current at X seconds, where X is 300 for fuse ratings below 100 amps and X is 600 for fuse ratings above 100 amps.
  The current rating is the level of current the fuse can safely carry for an indefinite period of time.
Explanation:

## Slide 180: Case III: Fault and Dynamic
ECpE Department
Fuse.dss file
New "Fuse.f1" MonitoredObj=Line.L6 MonitoredTerm=1 FuseCurve=Klink RatedCurrent=65
OpenDSS Code:
Explanation:
New "Fuse.f1"
Defines a fuse object named f1.
MonitoredObj
Specifies the full object name of the circuit element, typically a line, transformer, load, or generator, to which the Fuse is connected. This is the "monitored" element. There is no default; must be specified.
MonitoredTerm
Specifies the number of the terminal of the circuit element to which the Fuse is connected. 1 or 2, typically. Default is 1.

## Slide 181: Case III: Fault and Dynamic
ECpE Department
Fuse.dss file
New "Fuse.f1" MonitoredObj=Line.L6 MonitoredTerm=1 FuseCurve=Klink RatedCurrent=65
OpenDSS Code:
Explanation:
Fusecurve
Specifies the name of the TCC Curve object that determines the fuse blowing.
RatedCurrent
Specifies a multiplier or actual phase amps for the phase TCC curve. Defaults to 1.0.

## Slide 182: Case III: Fault and Dynamic
ECpE Department
Monitor.dss file
New "Monitor.cb1" element=Line.L1 terminal=1 mode=0
OpenDSS Code:
Explanation:
New "Monitor.cb1"
Defines a monitor object named cb1.
element
Specifies the name of an existing circuit element to which the monitor is to be connected.
mode
An integer bitmask code to describe what the monitor will save. Monitors can save two basic types of quantities: 1) Voltage and current; 2) Power. The Mode codes are defined as follows:
  0: Standard mode - V and I, each phase, complex
…
Specifies the number of the terminal to which the monitor will be connected.
terminal

## Slide 183: Case III: Fault and Dynamic
ECpE Department
Monitor.dss file
New "Monitor.cb1" element=Line.L1 terminal=1 mode=0
OpenDSS Code:
Explanation:
mode
…
  1: Power each phase, complex (kw and kvars)
  2: Transformer taps (connect Monitor to a transformer winding)
  3: State variables (connect Montor to a PCElement)
  4: Flicker level and severity index (Pst) for voltages.
  5: Solution variables (Iterations, etc). Normally, these would be actual phasor quantities from solution.
  6: Capacitor Switching
+16: Sequence components: V012, I012
+32: Magnitude only
+64: Positive Seqence only or Average of phases, if not 3 phases.
For example, Mode=33 (33=1+32) will save the magnitude of the power (kVA) only in each phase. Mode=112 (0+16+32+64) saves Positive sequence voltages and currents, magnitudes only.

## Slide 184
ECpE Department
Thank you!